## PumpSize
User Inputs - Edit yellow cells |  |  | Rev 2.14 - Sept 27-2021 | Design Targets
Location | USA-Wyoming-Rock Springs
Design Pressure (psi) | 2000 | PSI
Daily Volume required | 10 | US-Quarts/day |  | Q - L/day
Select Pump | COMET2-300, SH, 12 VDC |  |  | 9.4635 |  | Interp | Interp |  |  |  |  | Rated
Multipoint (0-15) | 0 |  | with Powersavers |  | Pump Selected | RPM | Watts | Panel Voltage | Pump Voltage | maxP | max RPM | max Flow | Min RPM
InSight - Closed Loop | No |  | with Powersavers | Design Pressure (psi) | [7 empty] | L/day
InSight - Connect | No |  | Cellular | 2000 | COMET2-300, SH, 12 VDC | 59.5263 | 13.8607 | 16 | 12 | 3000 | 1000 | 257.154 | 300
Sirius F2-MPPT Charge Controller | No |  | MPPT | 6.8948
Battery Capacity | 100 |  | AmpHrs
Lowest Battery Temp | -20C |  | -4 degF |  | Aux power Data Table
Minimum # of Days Autonomy (7-10 typ.) | 4 |  | days |  | Multipoint ( with Powersavers) | 0.5 | 0
Min Total Solar Panel Watts Required | 105.9802 |  | Watts |  | Insight Closed loop | 0.75 | 0 |  | Mean insolation | 21.4 | mJ/m2
Select Panel Size | 110 |  | Watts/Panel |  | Insight Connect | 0.5 | 0 |  | PV potential | 138 | kwhr/kw/mo july
Panel Nominal Voltage | 12 |  | Volts |  | Total Aux Power ( Wattts) |  | 0 |  |  | 5.9444 | kw/m2 |  | 0.96
[10 empty] | 4.4516 | kwhr/kw/day
Results
# Batteries Required | 2 |  | Batteries
Excess Battery Capacity | 26.26%
Final Autonomy | 5.0503 |  | Days | [6 empty] | 1.3353
Number of Panels | 1 |  | Panels |  | Solar Panel Operating Voltage (16V or 32V) | 16 |  | (VDC) |  | 0.74887 | performance factor 0.75
Ideal Panel Tilt | 56.6 |  | degrees from Horizontal
Excess Panel Capacity | 3.793% |  | Excess Panel Power | Max flow in xxx units | [5 empty] | Termperature Table |  |  |  | 3.2123 | WATTS HYDRAULIC
Warnings |  |  |  | 271.7319 | Current Factor | 0.94635 | Multiplexor | Current adder |  | -40C | -40 degF |  |  | 77.0942 | WATTHRS HYDRAULIC
[10 empty] | -30C | -22 degF
[5 empty] | Unit Conv | Factor | Yes | 0.83333 |  | -20C | -4 degF
[5 empty] | L/day | 1 | No | 0 |  | -10C | 14 degF |  |  | 7983.7474 | WATTHRS ELECTRIC
[5 empty] | US-Quarts/day | 0.94635 |  |  |  | >=0C | >= 32 degF |  |  | 0.0096564 | EFF
[5 empty] | US-Gal/day | 3.7854
Flow
Pump Mode | Intermitent
Max Rated Flow Rate per point | 271.7319 |  | US-Quarts/day | Check valve pressure | 40 | psi
% of Max Flow | 3.68% |  |  | Actual inj pressure | 2040 | psi
System Power
Draw at Design Pressure | 13.8607 |  | Watts
Aux Power | 0 |  | Watts |  |  | 345.2739 | Power Stored per Day per panel
Daily Energy Usage | 332.6561 |  | Watt-Hrs |  |  | 332.6561 | Daily power consumption of pump
Required Energy for total num days autonomy | 1330.6246 |  | Watt-Hrs |  |  | 1.0379
Battery Capacity for number days autonomy | 158.4077 |  | AmpHrs
Solar
Vertical Panel | 3.9 |  | Hrs/day sunlight - worst case |  |  | 4.1 | Insolation -- IF CANADA then verticle * Solar data Adjustment
At Ideal Panel Tilt angle | 4.1 |  | Hrs/day sunlight - worst case
Total Power Stored per day | 345.2739 |  | Watt-Hrs
|  |  |  | Solar Panel Data | 155W Heliene 36P poly
|  |  |  | Base PWM controller | 0.73679 | n - efficiency | 25C
|  |  |  | Base Sirius MPPT | 0.95 | n - efficiency | 25C
|  |  |  | Heliend 36P MAxP Temp coef | -0.43 | % Watts/ deg C
|  |  |  | Heliene 36P volt Temp coef | -0.32 | %Volts/degC
|  |  |  | MPP voltage | 18.73 | V
|  |  |  | Impp | 8.59 | A
|  |  |  | Isc ( short circuit) | 9.26 | A
|  |  |  | Std cond | 25 | C
|  |  |  | Winter Mid day avghi temp | -1 | C
|  |  |  | Batt Coef | -0.0039 | V/degC/cell
|  |  |  | Batt Coef | -0.0234 | volts/deg C
|  |  |  | Adj float Voltage 12V | 14.4084 | Volts
|  |  |  | Adj float voltage 24V | 28.8168 | Volts
|  |  |  | Adj MPP Panel Voltage | 20.2883
|  |  |  | Adjusted PWM n | 0.76557 | n - efficiency
|  |  |  | Adjusted MPPT n | 1.0562 | n - efficiency
|  |  |  | Ratio MPPT-n /PWM n | 1.3796
|  |  |  | Solar Data Adjustment ( 0.75 to 0.85 factor) | 1.25
Energy Harvedsted PWM
Energy Harvested MPPT
Additional Data
|  |  |  | MPPT/PWM Charge Reg Advantage | 1.3796
|  |  |  | Temperature Factor | 0.7
|  |  |  | Performance Factor - System efficency | 1
|  |  |  | Location Latitude | 41.6 |  | (deg North)
|  |  |  | Power Stored per Day per panel | 345.2739 |  | Watt-Hrs
|  |  |  | Daily power consumption of system | 332.6561 |  | Watt-Hrs
Flow-Spec Solar Sizing Software
(all rights reserved)

## CalData-FUS (hidden)
Data Summary Table |  | Data Summary Table |  | Interp |  |  | Max P | MaxFlow | CALCULATED Max Flow | InSight Compatable | Stack compatible | Min RPM | max flow | max flow | linear pump curve pressure/volume curve fit y = mx +b
Set | Name-datalist | Set | Row | rpm | Interp Watts | Voltage | psi | RPM | L/day |  |  |  | upper bound (L/D) | upper bound | m | b
0 | COMET2 100, DH, 24 VDC | 1 |  | 148.5684 | #DIV/0! | 32 | 1000 | 1000 | 601.368 | 0 | 0 | 300 |  |  | -0.6758 | 1980
1 | FUSION2 100, DH, 24 VDC | 2 |  | 1.3227 | #DIV/0! | 32 | 1000 | 600 | 1112.224 | 0 | 0 | 20 |  |  | -0.0544 | 1223.2
2 | FUSION2 150, SH, 12 VDC | 3 |  | 32.4382 | 10.4573 | 16 | 1500 | 166 | 47.3176 | 1 | 1 | 20 | 50 | 47.3176 | -0.0109 | 47.3176
3 | FUSION2 150, DH, 12 VDC | 4 |  | 13.5922 | 8.6575 | 16 | 1500 | 166 | 94.6352 | 1 | 1 | 20 | 100 | 94.6352 | -0.0218 | 94.6352
4 | FUSION2 150, SH, 24 VDC | 5 |  | 32.4382 | 10.4573 | 32 | 1500 | 166 | 47.3176 | 1 | 1 | 20 | 50 | 47.3176 | -0.0109 | 47.3176
5 | FUSION2 150, DH, 24 VDC | 6 |  | 13.5922 | 8.6575 | 32 | 1500 | 166 | 94.6352 | 1 | 1 | 20 | 100 | 94.6352 | -0.0218 | 94.6352
6 | FUSION2 300, SH, 12 VDC | 7 |  | 32.4382 | 10.4573 | 16 | 3000 | 300 | 74.0537 | 1 | 1 | 20 | 90 | 85.1717 | -0.00545 | 85.1717
7 | FUSION2 300, DH, 12 VDC | 8 |  | 13.5922 | 8.6575 | 16 | 3000 | 300 | 148.1074 | 1 | 1 | 20 | 180 | 170.3434 | -0.0109 | 170.3434
8 | FUSION2 300, SH, 24 VDC | 9 |  | 32.4382 | 10.4573 | 32 | 3000 | 600 | 148.1074 | 1 | 1 | 20 | 180 | 170.3434 | -0.0109 | 170.3434
9 | FUSION2 300, DH, 24 VDC | 10 |  | 13.5922 | 8.6575 | 32 | 3000 | 600 | 296.2147 | 1 | 1 | 20 | 360 | 340.6867 | -0.0218 | 340.6867
10 | FUSION2 500, SH, 12 VDC | 11 |  | 39.3517 | 7.6011 | 16 | 5000 | 300 | 50.3551 | 1 | 2 | 20 | 60 | 56.7811 | -0.00315 | 56.7811
11 | FUSION2 500, DH, 12 VDC | 12 |  | 15.9627 | 6.9567 | 16 | 5000 | 300 | 100.7102 | 1 | 2 | 20 | 120 | 113.5622 | -0.0063 | 113.5622
12 | FUSION2 500, SH, 24 VDC | 13 |  | 39.3517 | 7.6011 | 32 | 5000 | 600 | 100.7102 | 1 | 2 | 20 | 120 | 113.5622 | -0.0063 | 113.5622
13 | FUSION2 500, DH, 24 VDC | 14 |  | 15.9627 | 6.9567 | 32 | 5000 | 600 | 201.4205 | 1 | 2 | 20 | 240 | 227.1245 | -0.0126 | 227.1245
14 | COMET2-300, SH, 24 VDC | 15 |  | 59.5263 | 11.0885 | 32 | 3000 | 1000 | 257.154 | 1 | 1 | 300 |  |  | -0.0319 | 322.23
15 | COMET2-300, SH, 12 VDC | 16 |  | 59.5263 | 13.8607 | 16 | 3000 | 1000 | 257.154 | 1 | 1 | 300 |  |  | -0.0319 | 322.23
16 | COMET2-300, DH, 24 VDC | 17 |  | 24.5941 | 5.6762 | 32 | 3000 | 1000 | 421.74 | 1 | 1 | 300 |  |  | -0.0905 | 606.36
17 | COMET2-300, DH, 12 VDC | 18 |  | 24.5941 | 7.0952 | 16 | 3000 | 1000 | 421.74 | 1 | 1 | 300 |  |  | -0.0905 | 606.36
18 | COMET2-500, HP, DH, 24 VDC | 19 |  | 28.9796 | 4.9855 | 32 | 5000 | 1000 | 344.728 | 1 | 1 | 300 |  |  | -0.0493 | 445.3
0.94635
|  |  |  | FUSION Pump Type |  | SH-24V | DH-24V | SH-12V | DH-12V |  | Q/day | L/day
|  |  |  | FUSION2 150 | Rate | 50 Q/day | 100 Q/day | 50 Q/day | 100 Q/day |  | 50 | 47.3176
[5 empty] | Pressure | 1500 psi | 1500 psi | 1500 psi | 1500 psi |  | 90 | 85.1717
|  |  |  | FUSION2 300 | Rate | 180 Q/day | 360 Q/day | 90 Q/day | 180 Q/day |  | 100 | 94.6352
[5 empty] | Pressure | 3000 psi | 3000 psi | 3000 psi | 3000 psi |  | 180 | 170.3434
|  |  |  | FUSION2 500 | Rate | 120 Q/day | 240 Q/day | 60 Q/day | 120 Q/day |  | 360 | 340.6867 |  |  |  |  | 0 | 1980
[5 empty] | Pressure | 5000 psi | 5000 psi | 5000 psi | 5000 psi | [5 empty] | m | b | 1000 | 1304.2
|  |  |  | COMET2 100 | Rate | [5 empty] | 635.4591 | 601.368 |  |  | -0.6758 | 1980
[5 empty] | Pressure |  | 1000 psi | [7 empty] | linear pump curve pressure/volume curve fit y = mx +b
|  |  |  | FUSION2 100 | Rate |  | 1300 Q/d |  |  |  | 1299.7278 | 1230
[5 empty] | Pressure |  | 1000 psi
|  |  |  | 12V/24V Comet Motor Power |  | 1.25
24V comets are measured
12V comet motors are show to be 1.25 more watts due to
higher currents, winding, cable, and controller losses.
Note on G26: Hailey Meek: 12.5 G/day 47 L/day
Note on H26: Hailey Meek: 25 G/day 95 L/day
Note on I26: Hailey Meek: 12.5 G/day 47 L/day
Note on J26: Hailey Meek: 25 G/day 95 L/day
Note on G28: Hailey Meek: 45 G/day 170 L/day
Note on H28: Hailey Meek: 90 G/day 341 L/day
Note on I28: Hailey Meek: 22.5 G/day 85 L/day
Note on J28: Hailey Meek: 45 G/day 170 L/day
Note on G30: Hailey Meek: 30 G/day 114 L/day
Note on H30: Hailey Meek: 60 G/day 227 L/day
Note on I30: Hailey Meek: 15 G/day 57 L/day
Note on J30: Hailey Meek: 30 G/day 114 L/day

## SOLAR_DATA (hidden)
performance factor allows for conversion effiecinecy, cabling, and other losses.
for Canadian data
| Performance Factor = | 0.75 | http://198.103.48.154/fichier.php/codectec/Fr/2006-046/2006-046_OP-J_411-SOLRES_PV+map.pdf
https://glfc.cfsnet.nfis.org/mapserver/pv/municip.php?n=720&NEK=e
|  | PV Potential Worst Month kWh/kW/mo |  | PV Potential Best Month kWh/kW/mo |  | Area | Ideal Tilt | Ideal Tilt | Avg midday Dec-Jan temp
TOWN | Area | Verticle | Lat + 15deg | Verticle | Lat + 15 | Latitude | Lat+15 | Lat+15 | deg C | World map | http://worldmap.harvard.edu/maps/oilandgasmap
Athabasca | CDN-Athabasca | 58 | 58 | 72 | 101 | 54.7 | 69.7 | 70 | -9 | World map | http://solarelectricityhandbook.com/solar-irradiance.html
Bonnyville | CDN-Bonnyville | 61 | 61 | 71 | 101 | 54.3 | 69.3 | 70 | -10 | US solar data | in kWhrs/m2/day
Brooks | CDN-Brooks | 74 | 75 | 71 | 110 | 50.6 | 65.6 | 65 | -4 | http://rredc.nrel.gov/solar/pubs/redbook/ |  | X:\PRODUCTS\SIS\Flow Spec Software\USA Solar Data
Calgary | CDN-Calgary | 71 | 71 | 69 | 105 | 51 | 66 | 65 | -2 | Canada's data | kWhrs/kw/month | https://fgp-pgf.maps.arcgis.com/apps/webappviewer/index.html?id=c91106a7d8c446a19dd1909fd93645d3
Dawson Creek | CDN-Dawson Creek | 56 | 56 | 76 | 103 | 55.7 | 70.7 | 70 | -7 | http://pv.nrcan.gc.ca/index.php?n=720&m=u&lang=e
Drayton Valley | CDN-Drayton Valley | 56 | 56 | 70 | 100 | 53.2 | 68.2 | 70 | -5 | https://www.nrcan.gc.ca/energy/energy-sources-distribution/renewables/solar-photovoltaic-energy/solar-resource-data-available-canada/14390
Drumheller | CDN-Drumheller | 74 | 74 | 72 | 108 | 51.4 | 66.4 | 65 | -6
Edmonton | CDN-Edmonton | 63 | 63 | 72 | 103 | 53.6 | 68.6 | 70 | -7 | MidDay Temps - Weather
Edson | CDN-Edson | 53 | 53 | 70 | 100 | 53.6 | 68.6 | 70 | -6 | https://weatherspark.com/m/2795/1/Average-Weather-in-January-in-Fort-McMurray-Canada
Estevan | CDN-Estevan | 82 | 83 | 68 | 108 | 49.1 | 64.1 | 65 | -8
Fort McMurray | CDN-Fort McMurray | 54 | 53 | 73 | 99 | 56.7 | 71.7 | 70 | -12
Ft. Nelson | CDN-Ft. Nelson | 40 | 39 | 77 | 100 | 58.8 | 73.8 | 75 | -15
Grande Praire | CDN-Grande Praire | 56 | 56 | 74 | 102 | 55.1 | 70.1 | 70 | -8
High Level | CDN-High Level | 47 | 47 | 79 | 103 | 58.5 | 73.5 | 75 | -15
Lloydminster | CDN-Lloydminster | 65 | 65 | 70 | 103 | 53.3 | 68.3 | 70 | -10
Medicine Hat | CDN-Medicine Hat | 74 | 75 | 72 | 111 | 50 | 65 | 65 | -3
Pink Mountain | CDN-Pink Mountain | 45 | 45 | 74 | 98 | 57 | 72 | 70 | -15
Ponoka | CDN-Ponoka | 67 | 67 | 71 | 104 | 52.7 | 67.7 | 70 | -6
Prince George | CDN-Prince George | 38 | 38 | 71 | 99 | 53.9 | 68.9 | 70 | -5
Red Deer | CDN-Red Deer | 68 | 68 | 70 | 104 | 52.3 | 67.3 | 65 | -6
Rimbey | CDN-Rimbey | 63 | 63 | 70 | 103 | 52.6 | 67.6 | 70 | -6
Slave Lake | CDN-Slave Lake | 53 | 53 | 73 | 101 | 55.3 | 70.3 | 70 | -9
Swift Current | CDN-Swift Current | 73 | 73 | 71 | 110 | 50.3 | 65.3 | 65 | -6
Valleyview | CDN-Valleyview | 54 | 54 | 72 | 101 | 55 | 70 | 70 | -7
Weyburn | CDN-Weyburn | 81 | 81 | 69 | 109 | 49.6 | 64.6 | 65 | -8
Whitecourt | CDN-Whitecourt | 53 | 53 | 70 | 100 | 54.1 | 69.1 | 70 | -7
Arkansas - Ft Smith | USA-Arkansas - Ft Smith | 69 | 132 | 69 | 156 | 34.7 | 49.7 | 50 | 10
California-Bakersfield | USA-California-Bakersfield | 90 | 102 | 72 | 183 | 35.4 | 50.4 | 50 | 15
Colorado-Boulder | USA-Colorado-Boulder | 129 | 135 | 78 | 156 | 40 | 55 | 55 | 6
Louisiana-Shreveport | USA-Louisiana-Shreveport | 60 | 117 | 78 | 156 | 32.47 | 47.47 | 45 | 13
New Mexico-Albuquerque | USA-New Mexico-Albuquerque | 70 | 165 | 72 | 183 | 35 | 50 | 50 | 9
New Mexico-Artesia | USA-New Mexico-Artesia | 70 | 120 | 68 | 182 | 32.8 | 47.8 | 50 | 14
North Dakota-Minot | USA-North Dakota-Minot | 90 | 90 | 90 | 150 | 48.3 | 63.3 | 65 | -6
Oklahoma-OK city | USA-Oklahoma-OK city | 120 | 132 | 69 | 156 | 35.4 | 50.4 | 50 | 9
Pennsylvania-Williamsport | USA-Pennsylvania-Williamsport | 66 | 72 | 75 | 141 | 41.3 | 56.3 | 55 | 1
Texas-Amarillo | USA-Texas-Amarillo | 120 | 150 | 66 | 165 | 35.2 | 50.2 | 50 | 10
Texas-Corpus Christi | USA-Texas-Corpus Christi | 96 | 114 | 51 | 144 | 27 | 42 | 40 | 19
Texas--ElPaso | USA-Texas--ElPaso | 110 | 168 | 63 | 180 | 31.8 | 46.8 | 45 | 14
Texas--Ft.Worth | USA-Texas--Ft.Worth | 81 | 132 | 63 | 159 | 32.8 | 47.8 | 50 | 14
Texas-Midland | USA-Texas-Midland | 90 | 156 | 63 | 159 | 31.9 | 46.9 | 45 | 14
Texas-San Antonio | USA-Texas-San Antonio | 114 | 132 | 57 | 156 | 29.5 | 44.5 | 45 | 17
Texas--Tyler | USA-Texas--Tyler | 100 | 132 | 63 | 159 | 32.35 | 47.35 | 45 | 14
Wyoming-Rock Springs | USA-Wyoming-Rock Springs | 117 | 123 | 84 | 165 | 41.6 | 56.6 | 55 | -1
Argentina-Nequen | Argentina-Nequen | 84.9 | 103.5 |  |  | 38.9 | 53.9 | 55 | 12
Argentina-ComodoroRivadavia | Argentina-ComodoroRivadavia | 48 | 69 |  |  | 45.8 | 60.8 | 60 | 10
Argentina-RioGallegos | Argentina-RioGallegos | 33 | 36 |  |  | 51.6 | 66.6 | 65 | 4
Kuwait | Kuwait | 117.6 | 137.1 | 59.4 | 175.8 | 29.3 | 44.3 | 45 | 19
Malaysia | Malaysia-Miri | 63.9 | 151.2 | 52.5 | 148.8 | 4.4 | 19.4 | 20 | 30
Pakistan | Pakistan | 153 | 168 | 63 | 180 | 31.8 | 46.8 | 45 | 26

## COMET2_SH300 (hidden)
| Date | 2021-06-24 | Tech: satnam singh | 100 rpm data corrected july 27
glycol COMET2 pump - 24V comet motor | [14 empty] | RPMs | pressure
# Heads |  | single | [12 empty] | 100 | 0
Piston |  | 0.375 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 200 | 100 |  | min rpm
Supply V |  | 25.6 |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 400 | 500 |  | 300
Stroke |  | 0.136 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 600 | 1000
Head |  | standard | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 800 | 2000
head config |  | soft seat cartridge, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 1000 | 3000
Pressure |  | Power - ELEC |  |  | FLOW |  |  | measured | mech work | Effieciency |  |  |  |  | average rate |  |  |  | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve |  | duty cycle | L/d |  |  |  | 50 | 75
0 | 100 | 509 | 180 | 10.18 | 9.95 | 60 | 32 | 32 | 0 | 0% |  |  |  | 100% | 32
100 | 100 | 536 | 180 | 10.72 | 10.49 | 60 | 31 | 31 | 0.248 | 2.313% |  | 100% |  | 100% | 31 |  |  |  | 100 | 150
500 | 100 | 596 | 180 | 11.92 | 11.69 | 60 | 29 | 29 | 1.16 | 9.732% |  | 93.55% |  | 100% | 29 |  |  |  | 200 | 300
1000 | 100 | 696 | 180 | 13.92 | 13.69 | 60 | 28 | 28 | 2.24 | 16.09% |  | 90.32% |  | 100% | 28 |  |  |  | 300 | 450
2000 | 100 | 920 | 180 | 18.4 | 18.17 | 60 | 26 | 26 | 4.16 | 22.61% |  | 83.87% |  | 100% | 26 |  |  |  | 400 | 600
3000 | 100 | 1025 | 180 | 20.5 | 20.27 | 60 | 24 | 24 | 5.76 | 28.1% |  | 77.42% |  | 100% | 24
0 | 200 | 676 | 180 | 13.52 | 13.29 | 60 | 64 | 64 | 0 | 0% |  |  |  | 66.67% | 42.6667
100 | 200 | 753 | 180 | 15.06 | 14.83 | 60 | 62 | 62 | 0.496 | 3.293% |  | 100% |  | 66.67% | 41.3333 |  |  |  | 100 | 150
500 | 200 | 848 | 180 | 16.96 | 16.73 | 60 | 61 | 61 | 2.44 | 14.39% |  | 98.39% |  | 66.67% | 40.6667 |  |  |  | 200 | 300
1000 | 200 | 1086 | 180 | 21.72 | 21.49 | 60 | 57 | 57 | 4.56 | 20.99% |  | 91.94% |  | 66.67% | 38 |  |  |  | 300 | 450
2000 | 200 | 1561 | 180 | 31.22 | 30.99 | 60 | 53 | 53 | 8.48 | 27.16% |  | 85.48% |  | 66.67% | 35.3333 |  |  |  | 400 | 600
3000 | 200 | 1804 | 180 | 36.08 | 35.85 | 60 | 49 | 49 | 11.76 | 32.59% |  | 79.03% |  | 66.67% | 32.6667
0 | 400 | 668 | 120 | 20.04 | 19.81 | 37 | 80 | 129.7297 | 0 | 0%
100 | 400 | 769 | 120 | 23.07 | 22.84 | 38 | 80 | 126.3158 | 1.0105 | 4.38% |  | 100% | [6 empty] | 100 | 150
500 | 400 | 910 | 120 | 27.3 | 27.07 | 40 | 80 | 120 | 4.8 | 17.58% |  | 95% | [6 empty] | 200 | 300
1000 | 400 | 1163 | 120 | 34.89 | 34.66 | 41 | 80 | 117.0732 | 9.3659 | 26.84% |  | 92.68% | [6 empty] | 300 | 450
2000 | 400 | 1720 | 120 | 51.6 | 51.37 | 45 | 80 | 106.6667 | 17.0667 | 33.07% |  | 84.44% | [6 empty] | 400 | 600
3000 | 400 | 1822 | 120 | 54.66 | 54.43 | 49 | 80 | 97.9592 | 23.5102 | 43.01% |  | 77.55%
0 | 600 | 900 | 120 | 27 | 26.77 | 24.5 | 80 | 195.9184 | 0 | 0%
100 | 600 | 1025 | 120 | 30.75 | 30.52 | 25 | 80 | 192 | 1.536 | 4.995% |  | 100% | [6 empty] | 100 | 150
500 | 600 | 1234 | 120 | 37.02 | 36.79 | 26 | 80 | 184.6154 | 7.3846 | 19.95% |  | 96.15% | [6 empty] | 200 | 300
1000 | 600 | 1560 | 120 | 46.8 | 46.57 | 27 | 80 | 177.7778 | 14.2222 | 30.39% |  | 92.59% | [6 empty] | 300 | 450
2000 | 600 | 2170 | 120 | 65.1 | 64.87 | 30 | 80 | 160 | 25.6 | 39.32% |  | 83.33% | [6 empty] | 400 | 600
3000 | 600 | 2461 | 120 | 73.83 | 73.6 | 33 | 80 | 145.4545 | 34.9091 | 47.28% |  | 75.76%
0 | 800 | 580 | 60 | 34.8 | 34.57 | 17.75 | 80 | 270.4225 | 0 | 0%
100 | 800 | 628 | 60 | 37.68 | 37.45 | 18 | 80 | 266.6667 | 2.1333 | 5.662% |  | 100% | [6 empty] | 100 | 150
500 | 800 | 763 | 60 | 45.78 | 45.55 | 19 | 80 | 252.6316 | 10.1053 | 22.07% |  | 94.74% | [6 empty] | 200 | 300
1000 | 800 | 956 | 60 | 57.36 | 57.13 | 20 | 80 | 240 | 19.2 | 33.47% |  | 90% | [6 empty] | 300 | 450
2000 | 800 | 1298 | 60 | 77.88 | 77.65 | 23 | 80 | 208.6957 | 33.3913 | 42.88% |  | 78.26% | [6 empty] | 400 | 600
3000 | 800 | 1473 | 60 | 88.38 | 88.15 | 25 | 80 | 192 | 46.08 | 52.14% |  | 72%
0 | 1000 | 692 | 60 | 41.52 | 41.29 | 14.5 | 80 | 331.0345 | 0 | 0%
100 | 1000 | 800 | 60 | 48 | 47.77 | 15 | 80 | 320 | 2.56 | 5.333% |  | 100% | [6 empty] | 100 | 150
500 | 1000 | 941 | 60 | 56.46 | 56.23 | 16 | 80 | 300 | 12 | 21.25% |  | 93.75% | [6 empty] | 200 | 300
1000 | 1000 | 1125 | 60 | 67.5 | 67.27 | 17 | 80 | 282.3529 | 22.5882 | 33.46% |  | 88.24% | [6 empty] | 300 | 450
2000 | 1000 | 1503 | 60 | 90.18 | 89.95 | 18.4 | 80 | 260.8696 | 41.7391 | 46.28% |  | 81.52% | [6 empty] | 400 | 600
3000 | 1000 | 1802 | 60 | 108.12 | 107.89 | 21 | 80 | 228.5714 | 54.8571 | 50.74% |  | 71.43%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 100 | 200 | 400 | 600 | 800 | 1000
[10 empty] | 0 | 32 | 42.6667 | 129.7297 | 195.9184 | 270.4225 | 331.0345
[10 empty] | 100 | 31 | 41.3333 | 126.3158 | 192 | 266.6667 | 320
[10 empty] | 500 | 29 | 40.6667 | 120 | 184.6154 | 252.6316 | 300
[10 empty] | 1000 | 28 | 38 | 117.0732 | 177.7778 | 240 | 282.3529
[10 empty] | 2000 | 26 | 35.3333 | 106.6667 | 160 | 208.6957 | 260.8696
[10 empty] | 3000 | 24 | 32.6667 | 97.9592 | 145.4545 | 192 | 228.5714
[10 empty] | 2040 | 25.9968 | 35.4096 | 106.8097 | 160.425 | 213.28 | 257.1514 | L/day
[9 empty] | L/day | 9.4635 | 59.5263 | RPM
CF @ 500 psi | 1670 | L/day
| 1000 | RPM | [10 empty] | watts | flow | watts | flow
Enter Flow | 9.4635 | L/day | [10 empty] | 9.95 | 32 | 13.29 | 42.6667
Enter pressure | 2040 | 1000 | max | [9 empty] | 10.72 | 31 | 15.06 | 41.3333
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom | [8 empty] | 11.92 | 29 | 16.96 | 40.6667
Calc RPM | 59.5263 | [11 empty] | 13.92 | 28 | 21.72 | 38
P Corr RPM | 59.5263 | [11 empty] | 18.4 | 26 | 31.22 | 35.3333
Interpolation Table | [12 empty] | 20.5 | 24 | 36.08 | 32.6667
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 100 | 200 | 400 | 600 | 800 | 1000 | 10000
0 | 0.23 | 9.95 | 13.29 | 19.81 | 26.77 | 34.57 | 41.29 | 412.9 | 6.012
100 | 0.23 | 10.72 | 15.06 | 22.84 | 30.52 | 37.45 | 47.77 | 477.7 | 6.4701
500 | 0.23 | 11.92 | 16.96 | 27.07 | 36.79 | 45.55 | 56.23 | 562.3 | 7.1839
1000 | 0.23 | 13.92 | 21.72 | 34.66 | 46.57 | 57.13 | 67.27 | 672.7 | 8.3736
2000 | 0.23 | 18.4 | 31.22 | 51.37 | 64.87 | 77.65 | 89.95 | 899.5 | 11.0386
3000.1 | 0.23 | 20.5 | 36.08 | 54.43 | 73.6 | 88.15 | 107.89 | 1078.9 | 12.2878
Enter RPM | 59.5263 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 11.0885 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## COMET2_DH300 (hidden)
| Date | 2021-06-24 | Tech: satnam singh | Corrected 100 rpm data July 27
glycol COMET2 pump - 24V comet motor | [14 empty] | RPMs | pressure
# Heads |  | dual | [12 empty] | 100 | 0
Piston |  | 0.375 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 200 | 100 |  | min rpm
Supply V |  | 25.8 |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 400 | 500 |  | 300
Stroke |  | 0.136 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 600 | 1000
Head |  | standard | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 800 | 2000
head config |  | soft seat cartridge, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 1000 | 3000
Pressure |  | Power - ELEC |  |  | FLOW |  |  | measured | mech work | Effieciency |  |  |  |  | average rate |  |  |  | 10 | 15
PSI | RPM | mWhr | Sample Time (sec) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve |  | duty cycle | L/d |  |  |  | 50 | 75
0 | 100 | 410 | 180 | 8.2 | 7.97 | 60 | 62 | 62 | 0 | 0% |  |  |  | 100% | 62
100 | 100 | 491 | 180 | 9.82 | 9.59 | 60 | 57 | 57 | 0.456 | 4.644% |  | 100% |  | 100% | 57 |  |  |  | 100 | 150
500 | 100 | 580 | 180 | 11.6 | 11.37 | 60 | 53 | 53 | 2.12 | 18.28% |  | 92.98% |  | 100% | 53 |  |  |  | 200 | 300
1000 | 100 | 704 | 180 | 14.08 | 13.85 | 60 | 49 | 49 | 3.92 | 27.84% |  | 85.96% |  | 100% | 49 |  |  |  | 300 | 450
2000 | 100 | 1118 | 180 | 22.36 | 22.13 | 60 | 41 | 41 | 6.56 | 29.34% |  | 71.93% |  | 100% | 41 |  |  |  | 400 | 600
3000 | 100 | 1221 | 180 | 24.42 | 24.19 | 60 | 33 | 33 | 7.92 | 32.43% |  | 57.89% |  | 100% | 33
0 | 200 | 588 | 180 | 11.76 | 11.53 | 26 | 80 | 184.6154 | 0 | 0% |  |  |  | 66.67% | 123.0769
100 | 200 | 725 | 180 | 14.5 | 14.27 | 28 | 80 | 171.4286 | 1.3714 | 9.458% |  | 100% |  | 66.67% | 114.2857 |  |  |  | 100 | 150
500 | 200 | 895 | 180 | 17.9 | 17.67 | 30 | 80 | 160 | 6.4 | 35.75% |  | 93.33% |  | 66.67% | 106.6667 |  |  |  | 200 | 300
1000 | 200 | 1230 | 180 | 24.6 | 24.37 | 32 | 80 | 150 | 12 | 48.78% |  | 87.5% |  | 66.67% | 100 |  |  |  | 300 | 450
2000 | 200 | 2078 | 180 | 41.56 | 41.33 | 38 | 80 | 126.3158 | 20.2105 | 48.63% |  | 73.68% |  | 66.67% | 84.2105 |  |  |  | 400 | 600
3000 | 200 | 2335 | 180 | 46.7 | 46.47 | 40 | 80 | 120 | 28.8 | 61.67% |  | 70% |  | 66.67% | 80
0 | 400 | 699 | 120 | 20.97 | 20.74 | 19 | 80 | 252.6316 | 0 | 0%
100 | 400 | 844 | 120 | 25.32 | 25.09 | 20 | 80 | 240 | 1.92 | 7.583% |  | 100% | [6 empty] | 100 | 150
500 | 400 | 1065 | 120 | 31.95 | 31.72 | 21 | 80 | 228.5714 | 9.1429 | 28.62% |  | 95.24% | [6 empty] | 200 | 300
1000 | 400 | 1440 | 120 | 43.2 | 42.97 | 22 | 80 | 218.1818 | 17.4545 | 40.4% |  | 90.91% | [6 empty] | 300 | 450
2000 | 400 | 2160 | 120 | 64.8 | 64.57 | 28 | 80 | 171.4286 | 27.4286 | 42.33% |  | 71.43% | [6 empty] | 400 | 600
3000 | 400 | 2450 | 120 | 73.5 | 73.27 | 37 | 80 | 129.7297 | 31.1351 | 42.36% |  | 54.05%
0 | 600 | 935 | 120 | 28.05 | 27.82 | 12.5 | 80 | 384 | 0 | 0%
100 | 600 | 1119 | 120 | 33.57 | 33.34 | 13 | 80 | 369.2308 | 2.9538 | 8.799% |  | 100% | [6 empty] | 100 | 150
500 | 600 | 1457 | 120 | 43.71 | 43.48 | 14 | 80 | 342.8571 | 13.7143 | 31.38% |  | 92.86% | [6 empty] | 200 | 300
1000 | 600 | 1960 | 120 | 58.8 | 58.57 | 15 | 80 | 320 | 25.6 | 43.54% |  | 86.67% | [6 empty] | 300 | 450
2000 | 600 | 2769 | 120 | 83.07 | 82.84 | 19 | 80 | 252.6316 | 40.4211 | 48.66% |  | 68.42% | [6 empty] | 400 | 600
3000 | 600 | 3215 | 120 | 96.45 | 96.22 | 23 | 80 | 208.6957 | 50.087 | 51.93% |  | 56.52%
0 | 800 | 1161 | 120 | 34.83 | 34.6 | 9.2 | 80 | 521.7391 | 0 | 0%
100 | 800 | 1420 | 120 | 42.6 | 42.37 | 9.5 | 80 | 505.2632 | 4.0421 | 9.489% |  | 100% | [6 empty] | 100 | 150
500 | 800 | 1877 | 120 | 56.31 | 56.08 | 10 | 80 | 480 | 19.2 | 34.1% |  | 95% | [6 empty] | 200 | 300
1000 | 800 | 2516 | 120 | 75.48 | 75.25 | 11 | 80 | 436.3636 | 34.9091 | 46.25% |  | 86.36% | [6 empty] | 300 | 450
2000 | 800 | 3466 | 120 | 103.98 | 103.75 | 14 | 80 | 342.8571 | 54.8571 | 52.76% |  | 67.86% | [6 empty] | 400 | 600
3000 | 800 | 3951 | 120 | 118.53 | 118.3 | 18 | 80 | 266.6667 | 64 | 53.99% |  | 52.78%
0 | 1000 | 705 | 60 | 42.3 | 42.07 | 7.7 | 80 | 623.3766 | 0 | 0%
100 | 1000 | 872 | 60 | 52.32 | 52.09 | 8 | 80 | 600 | 4.8 | 9.174% |  | 100% | [6 empty] | 100 | 150
500 | 1000 | 1150 | 60 | 69 | 68.77 | 8.5 | 80 | 564.7059 | 22.5882 | 32.74% |  | 94.12% | [6 empty] | 200 | 300
1000 | 1000 | 1541 | 60 | 92.46 | 92.23 | 9 | 80 | 533.3333 | 42.6667 | 46.15% |  | 88.89% | [6 empty] | 300 | 450
2000 | 1000 | 2110 | 60 | 126.6 | 126.37 | 11 | 80 | 436.3636 | 69.8182 | 55.15% |  | 72.73% | [6 empty] | 400 | 600
3000 | 1000 | 2432 | 60 | 145.92 | 145.69 | 14 | 80 | 342.8571 | 82.2857 | 56.39% |  | 57.14%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 100 | 200 | 400 | 600 | 800 | 1000
[10 empty] | 0 | 62 | 123.0769 | 252.6316 | 384 | 521.7391 | 623.3766
[10 empty] | 100 | 57 | 114.2857 | 240 | 369.2308 | 505.2632 | 600
[10 empty] | 500 | 53 | 106.6667 | 228.5714 | 342.8571 | 480 | 564.7059
[10 empty] | 1000 | 49 | 100 | 218.1818 | 320 | 436.3636 | 533.3333
[10 empty] | 2000 | 41 | 84.2105 | 171.4286 | 252.6316 | 342.8571 | 436.3636
[10 empty] | 3000 | 33 | 80 | 129.7297 | 208.6957 | 266.6667 | 342.8571
[10 empty] | 2040 | 40.8007 | 88.4979 | 169.6831 | 258.4557 | 345.5045 | 431.6739 | L/day
[9 empty] | L/day | 9.4635 | 24.5941 | RPM
CF @ 500 psi | 1670 | L/day
| 1000 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 1000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 24.5941 | [10 empty] | 100 |  | 200
P Corr RPM | 24.5941 | [10 empty] | watts | flow | watts | flow
Interpolation Table | [11 empty] | 7.97 | 62 | 11.53 | 123.0769
Pressure |  |  |  | Watts Table |  |  | Interm |  |  |  |  | 9.82 | 57 | 14.5 | 114.2857
RPM | 0.1 | 100 | 200 | 400 | 600 | 800 | 1000 | 10000 |  |  |  | 11.6 | 53 | 17.9 | 106.6667
0 | 0.23 | 7.97 | 11.53 | 20.74 | 27.82 | 34.6 | 42.07 | 420.7 | 2.1277 |  |  | 14.08 | 49 | 24.6 | 100
100 | 0.23 | 9.82 | 14.5 | 25.09 | 33.34 | 42.37 | 52.09 | 520.9 | 2.5813 |  |  | 22.36 | 41 | 41.56 | 84.2105
500 | 0.23 | 11.6 | 17.9 | 31.72 | 43.48 | 56.08 | 68.77 | 687.7 | 3.0178 |  |  | 24.42 | 33 | 46.7 | 80
1000 | 0.23 | 14.08 | 24.6 | 42.97 | 58.57 | 75.25 | 92.23 | 922.3 | 3.6258
2000 | 0.23 | 22.36 | 41.56 | 64.57 | 82.84 | 103.75 | 126.37 | 1263.7 | 5.656
3000.1 | 0.23 | 24.42 | 46.7 | 73.27 | 96.22 | 118.3 | 145.69 | 1456.9 | 6.1611
Enter RPM | 24.5941 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 5.6762 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## COMET2_HP-DH500 (hidden)
| Date | 2021-06-24 | Tech: satnam singh
glycol COMET2 pump - 24V comet motor | [14 empty] | RPMs | pressure
# Heads |  | dual | [12 empty] | 100 | 0
Piston |  | 0.312 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 200 | 500 |  | min rpm
Supply V |  | 25.7 |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 400 | 1000 |  | 300
Stroke |  | 0.136 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 600 | 3000
Head |  | HP Soft Seat w bleed | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 800 | 4000
head config |  | soft seat cartridge, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 1000 | 5000
Pressure |  | Power - ELEC |  |  | FLOW |  |  | measured | mech work | Effieciency | [8 empty] | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve | [6 empty] | 50 | 75
0 | 100 | 370 | 180 | 7.4 | 7.17 | 60 | 44 | 44 | 0 | 0%
500 | 100 | 479 | 180 | 9.58 | 9.35 | 60 | 40 | 40 | 1.6 | 16.7% |  | 100% | [6 empty] | 100 | 150
1000 | 100 | 600 | 180 | 12 | 11.77 | 60 | 37 | 37 | 2.96 | 24.67% |  | 92.5% | [6 empty] | 200 | 300
3000 | 100 | 1050 | 180 | 21 | 20.77 | 60 | 30 | 30 | 7.2 | 34.29% |  | 75% | [6 empty] | 300 | 450
4000 | 100 | 1255 | 180 | 25.1 | 24.87 | 60 | 26 | 26 | 8.32 | 33.15% |  | 65% | [6 empty] | 400 | 600
5000 | 100 | 1318 | 180 | 26.36 | 26.13 | 60 | 23 | 23 | 9.2 | 34.9% |  | 57.5%
0 | 200 | 434 | 180 | 8.68 | 8.45 | 60 | 87 | 87 | 0 | 0%
500 | 200 | 684 | 180 | 13.68 | 13.45 | 60 | 78 | 78 | 3.12 | 22.81% |  | 100% | [6 empty] | 100 | 150
1000 | 200 | 938 | 180 | 18.76 | 18.53 | 60 | 73 | 73 | 5.84 | 31.13% |  | 93.59% | [6 empty] | 200 | 300
3000 | 200 | 2066 | 180 | 41.32 | 41.09 | 60 | 62 | 62 | 14.88 | 36.01% |  | 79.49% | [6 empty] | 300 | 450
4000 | 200 | 2314 | 180 | 46.28 | 46.05 | 60 | 54 | 54 | 17.28 | 37.34% |  | 69.23% | [6 empty] | 400 | 600
5000 | 200 | 2450 | 180 | 49 | 48.77 | 60 | 46 | 46 | 18.4 | 37.55% |  | 58.97%
0 | 400 | 627 | 120 | 18.81 | 18.58 | 15 | 44 | 176 | 0 | 0%
500 | 400 | 910 | 120 | 27.3 | 27.07 | 15 | 39 | 156 | 6.24 | 22.86% |  | 100% | [6 empty] | 100 | 150
1000 | 400 | 1150 | 120 | 34.5 | 34.27 | 15 | 37 | 148 | 11.84 | 34.32% |  | 94.87% | [6 empty] | 200 | 300
3000 | 400 | 2150 | 120 | 64.5 | 64.27 | 15 | 29 | 116 | 27.84 | 43.16% |  | 74.36% | [6 empty] | 300 | 450
4000 | 400 | 2430 | 120 | 72.9 | 72.67 | 44 | 75 | 102.2727 | 32.7273 | 44.89% |  | 65.56% | [6 empty] | 400 | 600
5000 | 400 | 2634 | 120 | 79.02 | 78.79 | 30 | 48 | 96 | 38.4 | 48.6% |  | 61.54%
0 | 600 | 827 | 120 | 24.81 | 24.58 | 15 | 69 | 276 | 0 | 0%
500 | 600 | 1190 | 120 | 35.7 | 35.47 | 15 | 64 | 256 | 10.24 | 28.68% |  | 100% | [6 empty] | 100 | 150
1000 | 600 | 1575 | 120 | 47.25 | 47.02 | 15 | 60 | 240 | 19.2 | 40.63% |  | 93.75% | [6 empty] | 200 | 300
3000 | 600 | 2960 | 130 | 81.9692 | 81.7392 | 15 | 46 | 184 | 44.16 | 53.87% |  | 71.88% | [6 empty] | 300 | 450
4000 | 600 | 3066 | 120 | 91.98 | 91.75 | 15 | 38 | 152 | 48.64 | 52.88% |  | 59.38% | [6 empty] | 400 | 600
5000 | 600 | 3745 | 133 | 101.3684 | 101.1384 | 30 | 73 | 146 | 58.4 | 57.61% |  | 57.03%
0 | 800 | 1045 | 120 | 31.35 | 31.12 | 15 | 93 | 372 | 0 | 0%
500 | 800 | 1555 | 120 | 46.65 | 46.42 | 15 | 84 | 336 | 13.44 | 28.81% |  | 100% | [6 empty] | 100 | 150
1000 | 800 | 2070 | 120 | 62.1 | 61.87 | 15 | 77 | 308 | 24.64 | 39.68% |  | 91.67% | [6 empty] | 200 | 300
3000 | 800 | 3376 | 120 | 101.28 | 101.05 | 15 | 59 | 236 | 56.64 | 55.92% |  | 70.24% | [6 empty] | 300 | 450
4000 | 800 | 1953 | 60 | 117.18 | 116.95 | 15 | 50 | 200 | 64 | 54.62% |  | 59.52% | [6 empty] | 400 | 600
5000 | 800 | 2075 | 60 | 124.5 | 124.27 | 15 | 42 | 168 | 67.2 | 53.98% |  | 50%
0 | 1000 | 685 | 60 | 41.1 | 40.87 | 10 | 78 | 468 | 0 | 0%
500 | 1000 | 1202 | 75 | 57.696 | 57.466 | 10 | 70 | 420 | 16.8 | 29.12% |  | 100% | [6 empty] | 100 | 150
1000 | 1000 | 1249 | 60 | 74.94 | 74.71 | 10 | 62 | 372 | 29.76 | 39.71% |  | 88.57% | [6 empty] | 200 | 300
3000 | 1000 | 2082 | 60 | 124.92 | 124.69 | 10 | 49 | 294 | 70.56 | 56.48% |  | 70% | [6 empty] | 300 | 450
4000 | 1000 | 1050 | 30 | 126 | 125.77 | 10 | 40 | 240 | 76.8 | 60.95% |  | 57.14% | [6 empty] | 400 | 600
5000 | 1000 | 2568 | 60 | 154.08 | 153.85 | 15 | 53 | 212 | 84.8 | 55.04% |  | 50.48%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 100 | 200 | 400 | 600 | 800 | 1000
[10 empty] | 0 | 44 | 87 | 176 | 276 | 372 | 468
[10 empty] | 500 | 40 | 78 | 156 | 256 | 336 | 420
[10 empty] | 1000 | 37 | 73 | 148 | 240 | 308 | 372
[10 empty] | 3000 | 30 | 62 | 116 | 184 | 236 | 294
[10 empty] | 4000 | 26 | 54 | 102.2727 | 152 | 200 | 240
[10 empty] | 5000 | 23 | 46 | 96 | 146 | 168 | 212
[10 empty] | 2040 | 34.1784 | 68.236 | 135.6384 | 214.6687 | 278.2592 | 344.69 | L/day
[9 empty] | L/day | 9.4635 | 28.9796 | RPM
CF @ 500 psi | 1670 | L/day
| 1000 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 1000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 28.9796
P Corr RPM | 28.9796
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 100 | 200 | 400 | 600 | 800 | 1000 | 10000
0 | 0.23 | 7.17 | 8.45 | 18.58 | 24.58 | 31.12 | 40.87 | 408.7 | 2.2363
500 | 0.23 | 9.58 | 13.68 | 27.07 | 35.47 | 46.42 | 57.466 | 574.66 | 2.9329
1000 | 0.23 | 12 | 18.76 | 34.27 | 47.02 | 61.87 | 74.71 | 747.1 | 3.6325
3000 | 0.23 | 21 | 41.32 | 64.27 | 81.7392 | 101.05 | 124.69 | 1246.9 | 6.2343
4000 | 0.23 | 25.1 | 46.28 | 72.67 | 91.75 | 116.95 | 125.77 | 1257.7 | 7.4196
5000.1 | 0.23 | 26.36 | 49 | 78.79 | 101.1384 | 124.27 | 153.85 | 1538.5 | 7.7838
Enter RPM | 28.9796 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 4.9855 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## F2_300_SH (hidden)
| Date | 2021-04-16 | Tech: Blair Boone
FUSION2 300 pump - 24V fusion2 motor | [14 empty] | RPMs | pressure
# Heads |  | Single | [12 empty] | 20 | 0
Piston |  | 0.375 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 136 | 100
Supply V |  | 25.9 |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 252 | 500
Stroke |  | 0.15 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 368 | 1000
Head |  | soft seat, cartridge valve, bleeder head | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 484 | 2000
head config |  | soft seat poppet suction, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 600 | 3000
Pressure |  | Power - ELEC |  |  | FLOW |  |  |  | mech work | Effieciency | [7 empty] | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve | [5 empty] | 50 | 75
0 | 20 |  | 1 | 0 | -0.23 | 60 | 7.5 | 7.5 | 0 | #DIV/0!
100 | 20 | 78 | 1 | 4.68 | 4.45 | 60 | 7.5 | 7.5 | 0.06 | 1.282% |  | 100% | [5 empty] | 100 | 150
500 | 20 | 85 | 1 | 5.1 | 4.87 | 60 | 7.5 | 7.5 | 0.3 | 5.882% |  | 100% | [5 empty] | 200 | 300
1000 | 20 | 101 | 1 | 6.06 | 5.83 | 60 | 6.5 | 6.5 | 0.52 | 8.581% |  | 86.67% | [5 empty] | 300 | 450
2000 | 20 | 148 | 1 | 8.88 | 8.65 | 60 | 6 | 6 | 0.96 | 10.81% |  | 80% | [5 empty] | 400 | 600
3000 | 20 | 207 | 1 | 12.42 | 12.19 | 60 | 6 | 6 | 1.44 | 11.59% |  | 80%
0 | 136 | 187 | 1 | 11.22 | 10.99 | 60 | 46 | 46 | 0 | 0%
100 | 136 | 206 | 1 | 12.36 | 12.13 | 60 | 45 | 45 | 0.36 | 2.913% |  | 100% | [5 empty] | 100 | 150
500 | 136 | 233 | 1 | 13.98 | 13.75 | 60 | 44 | 44 | 1.76 | 12.59% |  | 97.78% | [5 empty] | 200 | 300
1000 | 136 | 264 | 1 | 15.84 | 15.61 | 60 | 43 | 43 | 3.44 | 21.72% |  | 95.56% | [5 empty] | 300 | 450
2000 | 136 | 369 | 1 | 22.14 | 21.91 | 60 | 42 | 42 | 6.72 | 30.35% |  | 93.33% | [5 empty] | 400 | 600
3000 | 136 | 482 | 1 | 28.92 | 28.69 | 60 | 40 | 40 | 9.6 | 33.2% |  | 88.89%
0%
0 | 252 | 297 | 1 | 17.82 | 17.59 | 60 | 85 | 85 | 0 | 0%
100 | 252 | 323 | 1 | 19.38 | 19.15 | 60 | 83 | 83 | 0.664 | 3.426% |  | 100% | [5 empty] | 100 | 150
500 | 252 | 369 | 1 | 22.14 | 21.91 | 60 | 82 | 82 | 3.28 | 14.81% |  | 98.8% | [5 empty] | 200 | 300
1000 | 252 | 435 | 1 | 26.1 | 25.87 | 60 | 80 | 80 | 6.4 | 24.52% |  | 96.39% | [5 empty] | 300 | 450
2000 | 252 | 584 | 1 | 35.04 | 34.81 | 60 | 76 | 76 | 12.16 | 34.7% |  | 91.57% | [5 empty] | 400 | 600
3000 | 252 | 751 | 1 | 45.06 | 44.83 | 60 | 75 | 75 | 18 | 39.95% |  | 90.36%
0 | 368 | 411 | 1 | 24.66 | 24.43 | 60 | 125 | 125 | 0 | 0%
100 | 368 | 441 | 1 | 26.46 | 26.23 | 60 | 125 | 125 | 1 | 3.779% |  | 100% | [5 empty] | 100 | 150
500 | 368 | 498 | 1 | 29.88 | 29.65 | 60 | 120 | 120 | 4.8 | 16.06% |  | 96% | [5 empty] | 200 | 300
1000 | 368 | 591 | 1 | 35.46 | 35.23 | 60 | 120 | 120 | 9.6 | 27.07% |  | 96% | [5 empty] | 300 | 450
2000 | 368 | 815 | 1 | 48.9 | 48.67 | 60 | 110 | 110 | 17.6 | 35.99% |  | 88% | [5 empty] | 400 | 600
3000 | 368 | 1025 | 1 | 61.5 | 61.27 | 60 | 110 | 110 | 26.4 | 42.93% |  | 88%
0 | 484 | 526 | 1 | 31.56 | 31.33 | 60 | 165 | 165 | 0 | 0%
100 | 484 | 574 | 1 | 34.44 | 34.21 | 60 | 165 | 165 | 1.32 | 3.833% |  | 100% | [5 empty] | 100 | 150
500 | 484 | 658 | 1 | 39.48 | 39.25 | 60 | 160 | 160 | 6.4 | 16.21% |  | 96.97% | [5 empty] | 200 | 300
1000 | 484 | 796 | 1 | 47.76 | 47.53 | 60 | 155 | 155 | 12.4 | 25.96% |  | 93.94% | [5 empty] | 300 | 450
2000 | 484 | 1056 | 1 | 63.36 | 63.13 | 60 | 150 | 150 | 24 | 37.88% |  | 90.91% | [5 empty] | 400 | 600
3000 | 484 | 1284 | 1 | 77.04 | 76.81 | 60 | 145 | 145 | 34.8 | 45.17% |  | 87.88%
0 | 600 | 673 | 1 | 40.38 | 40.15 | 60 | 205 | 205 | 0 | 0%
100 | 600 | 733 | 1 | 43.98 | 43.75 | 60 | 200 | 200 | 1.6 | 3.638% |  | 100% | [5 empty] | 100 | 150
500 | 600 | 817 | 1 | 49.02 | 48.79 | 60 | 200 | 200 | 8 | 16.32% |  | 100% | [5 empty] | 200 | 300
1000 | 600 | 971 | 1 | 58.26 | 58.03 | 60 | 195 | 195 | 15.6 | 26.78% |  | 97.5% | [5 empty] | 300 | 450
2000 | 600 | 1320 | 1 | 79.2 | 78.97 | 60 | 185 | 185 | 29.6 | 37.37% |  | 92.5% | [5 empty] | 400 | 600
3000 | 600 | 1402 | 1 | 84.12 | 83.89 | 60 | 180 | 180 | 43.2 | 51.36% |  | 90%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 20 | 136 | 252 | 368 | 484 | 600
[10 empty] | 0 | 7.5 | 46 | 85 | 125 | 165 | 205
[10 empty] | 100 | 7.5 | 45 | 83 | 125 | 165 | 200
[10 empty] | 500 | 7.5 | 44 | 82 | 120 | 160 | 200
[10 empty] | 1000 | 6.5 | 43 | 80 | 120 | 155 | 195
[10 empty] | 2000 | 6 | 42 | 76 | 110 | 150 | 185
[10 empty] | 3000 | 6 | 40 | 75 | 110 | 145 | 180
[10 empty] | 2040 | 6.2828 | 41.6548 | 77.105 | 113.1633 | 150.2881 | 186.5795 | L/day
[9 empty] | L/day | 9.4635 | 32.4382 | RPM
CF @ 500 psi | 1230 | L/day
| 600 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 1000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 32.4382
P Corr RPM | 32.4382
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 20 | 136 | 252 | 368 | 484 | 600 | 6000
0 | 0.23 | -0.23 | 10.99 | 17.59 | 24.43 | 31.33 | 40.15 | 401.5 | 0.97307
100 | 0.23 | 4.68 | 12.36 | 19.15 | 26.23 | 34.21 | 43.75 | 437.5 | 5.5035
500 | 0.23 | 5.1 | 13.98 | 21.91 | 29.65 | 39.25 | 48.79 | 487.9 | 6.0522
1000 | 0.23 | 6.06 | 15.84 | 25.87 | 35.23 | 47.53 | 58.03 | 580.3 | 7.1087
2000 | 0.23 | 8.88 | 22.14 | 34.81 | 48.67 | 63.13 | 78.97 | 789.7 | 10.3018
3000.1 | 0.23 | 12.42 | 28.92 | 44.83 | 61.27 | 76.81 | 83.89 | 838.9 | 14.1892
Enter RPM | 32.4382 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 10.4573 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## F2_300_DH (hidden)
| Date | 2021-04-16 | Tech: Blair Boone
FUSION2 300 pump - 24V fusion2 motor | [14 empty] | RPMs | pressure
# Heads |  | Dual | [12 empty] | 20 | 0
Piston |  | 0.375 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 136 | 100
Supply V |  | 25.9 |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 252 | 500
Stroke |  | 0.15 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 368 | 1000
Head |  | soft seat, cartridge valve, bleeder head | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 484 | 2000
head config |  | soft seat poppet suction, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 600 | 3000
Pressure |  | Power - ELEC |  |  | FLOW |  |  |  | mech work | Effieciency | [7 empty] | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve | [5 empty] | 50 | 75
0 | 20 | 65 | 1 | 3.9 | 3.67 | 60 | 14 | 14 | 0 | 0%
100 | 20 | 76 | 1 | 4.56 | 4.33 | 60 | 13 | 13 | 0.104 | 2.281% |  | 100% | [5 empty] | 100 | 150
500 | 20 | 95 | 1 | 5.7 | 5.47 | 60 | 13 | 13 | 0.52 | 9.123% |  | 100% | [5 empty] | 200 | 300
1000 | 20 | 131 | 1 | 7.86 | 7.63 | 60 | 13 | 13 | 1.04 | 13.23% |  | 100% | [5 empty] | 300 | 450
2000 | 20 | 207 | 1 | 12.42 | 12.19 | 60 | 12 | 12 | 1.92 | 15.46% |  | 92.31% | [5 empty] | 400 | 600
3000 | 20 | 307 | 1 | 18.42 | 18.19 | 60 | 11 | 11 | 2.64 | 14.33% |  | 84.62%
0 | 136 | 193 | 1 | 11.58 | 11.35 | 60 | 95 | 95 | 0 | 0%
100 | 136 | 230 | 1 | 13.8 | 13.57 | 60 | 90 | 90 | 0.72 | 5.217% |  | 100% | [5 empty] | 100 | 150
500 | 136 | 282 | 1 | 16.92 | 16.69 | 60 | 90 | 90 | 3.6 | 21.28% |  | 100% | [5 empty] | 200 | 300
1000 | 136 | 372 | 1 | 22.32 | 22.09 | 60 | 90 | 90 | 7.2 | 32.26% |  | 100% | [5 empty] | 300 | 450
2000 | 136 | 637 | 1 | 38.22 | 37.99 | 60 | 85 | 85 | 13.6 | 35.58% |  | 94.44% | [5 empty] | 400 | 600
3000 | 136 | 867 | 1 | 52.02 | 51.79 | 60 | 80 | 80 | 19.2 | 36.91% |  | 88.89%
0%
0 | 252 | 322 | 1 | 19.32 | 19.09 | 60 | 175 | 175 | 0 | 0%
100 | 252 | 378 | 1 | 22.68 | 22.45 | 60 | 170 | 170 | 1.36 | 5.996% |  | 100% | [5 empty] | 100 | 150
500 | 252 | 462 | 1 | 27.72 | 27.49 | 60 | 165 | 165 | 6.6 | 23.81% |  | 97.06% | [5 empty] | 200 | 300
1000 | 252 | 593 | 1 | 35.58 | 35.35 | 60 | 160 | 160 | 12.8 | 35.98% |  | 94.12% | [5 empty] | 300 | 450
2000 | 252 | 882 | 1 | 52.92 | 52.69 | 60 | 155 | 155 | 24.8 | 46.86% |  | 91.18% | [5 empty] | 400 | 600
3000 | 252 | 1230 | 1 | 73.8 | 73.57 | 60 | 150 | 150 | 36 | 48.78% |  | 88.24%
0 | 368 | 435 | 1 | 26.1 | 25.87 | 60 | 250 | 250 | 0 | 0%
100 | 368 | 542 | 1.0333 | 31.471 | 31.241 | 60 | 245 | 245 | 1.96 | 6.228% |  | 100% | [5 empty] | 100 | 150
500 | 368 | 761 | 1.2 | 38.05 | 37.82 | 60 | 240 | 240 | 9.6 | 25.23% |  | 97.96% | [5 empty] | 200 | 300
1000 | 368 | 813 | 1 | 48.78 | 48.55 | 60 | 235 | 235 | 18.8 | 38.54% |  | 95.92% | [5 empty] | 300 | 450
2000 | 368 | 1199 | 1 | 71.94 | 71.71 | 60 | 225 | 225 | 36 | 50.04% |  | 91.84% | [5 empty] | 400 | 600
3000 | 368 | 1605 | 1 | 96.3 | 96.07 | 60 | 215 | 215 | 51.6 | 53.58% |  | 87.76%
0 | 484 | 778 | 1.3833 | 33.7446 | 33.5146 | 60 | 335 | 335 | 0 | 0%
100 | 484 | 813 | 1.2167 | 40.0932 | 39.8632 | 60 | 325 | 325 | 2.6 | 6.485% |  | 100% | [5 empty] | 100 | 150
500 | 484 | 1037 | 1.25 | 49.776 | 49.546 | 60 | 320 | 320 | 12.8 | 25.72% |  | 98.46% | [5 empty] | 200 | 300
1000 | 484 | 1348 | 1.2667 | 63.8526 | 63.6226 | 60 | 310 | 310 | 24.8 | 38.84% |  | 95.38% | [5 empty] | 300 | 450
2000 | 484 | 1669 | 1.15 | 87.0783 | 86.8483 | 60 | 295 | 295 | 47.2 | 54.2% |  | 90.77% | [5 empty] | 400 | 600
3000 | 484 | 2059 | 1.0333 | 119.5548 | 119.3248 | 60 | 285 | 285 | 68.4 | 57.21% |  | 87.69%
0 | 600 | 821 | 1.2167 | 40.4877 | 40.2577 | 60 | 410 | 410 | 0 | 0%
100 | 600 | 960 | 1.1667 | 49.3714 | 49.1414 | 60 | 405 | 405 | 3.24 | 6.563% |  | 100% | [5 empty] | 100 | 150
500 | 600 | 1195 | 1.2167 | 58.9315 | 58.7015 | 60 | 395 | 395 | 15.8 | 26.81% |  | 97.53% | [5 empty] | 200 | 300
1000 | 600 | 1778 | 1.3833 | 77.1181 | 76.8881 | 60 | 390 | 390 | 31.2 | 40.46% |  | 96.3% | [5 empty] | 300 | 450
2000 | 600 | 2562 | 1.3833 | 111.1229 | 110.8929 | 60 | 360 | 360 | 57.6 | 51.83% |  | 88.89% | [5 empty] | 400 | 600
3000 | 600 | 2402 | 1 | 144.12 | 143.89 | 60 | 345 | 345 | 82.8 | 57.45% |  | 85.19%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 20 | 136 | 252 | 368 | 484 | 600
[10 empty] | 0 | 14 | 95 | 175 | 250 | 335 | 410
[10 empty] | 100 | 13 | 90 | 170 | 245 | 325 | 405
[10 empty] | 500 | 13 | 90 | 165 | 240 | 320 | 395
[10 empty] | 1000 | 13 | 90 | 160 | 235 | 310 | 390
[10 empty] | 2000 | 12 | 85 | 155 | 225 | 295 | 360
[10 empty] | 3000 | 11 | 80 | 150 | 215 | 285 | 345
[10 empty] | 2040 | 11.8878 | 84.439 | 155.3829 | 224.7271 | 296.9624 | 363.6881 | L/day
[9 empty] | L/day | 9.4635 | 13.5922 | RPM
CF @ 500 psi | 1230 | L/day
| 600 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 1000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 13.5922
P Corr RPM | 13.5922
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 20 | 136 | 252 | 368 | 484 | 600 | 6000
0 | 0.23 | 3.67 | 11.35 | 19.09 | 25.87 | 33.5146 | 40.2577 | 402.5767 | 2.5623
100 | 0.23 | 4.56 | 13.8 | 22.45 | 31.241 | 39.8632 | 49.1414 | 491.4143 | 3.1657
500 | 0.23 | 5.7 | 16.92 | 27.49 | 37.82 | 49.546 | 58.7015 | 587.0151 | 3.9387
1000 | 0.23 | 7.86 | 22.32 | 35.35 | 48.55 | 63.6226 | 76.8881 | 768.8807 | 5.4031
2000 | 0.23 | 12.42 | 38.22 | 52.69 | 71.71 | 86.8483 | 110.8929 | 1108.9289 | 8.4948
3000.1 | 0.23 | 18.42 | 52.02 | 73.57 | 96.07 | 119.3248 | 143.89 | 1438.9 | 12.5628
Enter RPM | 13.5922 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 8.6575 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## F2_500_SH (hidden)
| Date | 2021-05-03 | Tech: Blair Boone
glycol f2-500 - 24V fusion2 motor | [14 empty] | RPMs | pressure
# Heads |  | single | [12 empty] | 20 | 0
Piston |  | 0.3125 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 136 | 500
Supply V |  | 25.0 V |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 252 | 1000
Stroke |  | 0.136 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 368 | 3000
Head |  | high pressure | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 484 | 4000
head config |  | soft seat cartridge |  |  |  | Maintaining constant RPM | [8 empty] | 600 | 5000
Pressure |  | Power - ELEC |  |  | FLOW |  |  |  | mech work | Effieciency | [7 empty] | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve | [5 empty] | 50 | 75
0 | 20 | 144 | 3 | 2.88 | 2.65 | 180 | 16.5 | 5.5 | 0 | 0%
500 | 20 | 156 | 3 | 3.12 | 2.89 | 180 | 16.5 | 5.5 | 0.22 | 7.051% |  | 100% | [5 empty] | 100 | 150
1000 | 20 | 192 | 3 | 3.84 | 3.61 | 180 | 15 | 5 | 0.4 | 10.42% |  | 90.91% | [5 empty] | 200 | 300
3000 | 20 | 324 | 3 | 6.48 | 6.25 | 180 | 13.5 | 4.5 | 1.08 | 16.67% |  | 81.82% | [5 empty] | 300 | 450
4000 | 20 | 537 | 3 | 10.74 | 10.51 | 180 | 13.5 | 4.5 | 1.44 | 13.41% |  | 81.82% | [5 empty] | 400 | 600
5000 | 20 | 733 | 3 | 14.66 | 14.43 | 180 | 12 | 4 | 1.6 | 10.91% |  | 72.73%
0 | 136 | 200 | 1 | 12 | 11.77 | 60 | 34 | 34 | 0 | 0%
500 | 136 | 212 | 1 | 12.72 | 12.49 | 60 | 32 | 32 | 1.28 | 10.06% |  | 100% | [5 empty] | 100 | 150
1000 | 136 | 287 | 1 | 17.22 | 16.99 | 60 | 31 | 31 | 2.48 | 14.4% |  | 96.88% | [5 empty] | 200 | 300
3000 | 136 | 361 | 1 | 21.66 | 21.43 | 60 | 29 | 29 | 6.96 | 32.13% |  | 90.62% | [5 empty] | 300 | 450
4000 | 136 | 432 | 1 | 25.92 | 25.69 | 60 | 28 | 28 | 8.96 | 34.57% |  | 87.5% | [5 empty] | 400 | 600
5000 | 136 | 521 | 1 | 31.26 | 31.03 | 60 | 27 | 27 | 10.8 | 34.55% |  | 84.38%
0 | 252 | 275 | 1 | 16.5 | 16.27 | 60 | 57 | 57 | 0 | 0%
500 | 252 | 313 | 1 | 18.78 | 18.55 | 60 | 55 | 55 | 2.2 | 11.71% |  | 100% | [5 empty] | 100 | 150
1000 | 252 | 361 | 1 | 21.66 | 21.43 | 60 | 55 | 55 | 4.4 | 20.31% |  | 100% | [5 empty] | 200 | 300
3000 | 252 | 549 | 1 | 32.94 | 32.71 | 60 | 53 | 53 | 12.72 | 38.62% |  | 96.36% | [5 empty] | 300 | 450
4000 | 252 | 660 | 1 | 39.6 | 39.37 | 60 | 52 | 52 | 16.64 | 42.02% |  | 94.55% | [5 empty] | 400 | 600
5000 | 252 | 778 | 1 | 46.68 | 46.45 | 60 | 50 | 50 | 20 | 42.84% |  | 90.91%
0 | 368 | 373 | 1 | 22.38 | 22.15 | 60 | 83 | 83 | 0 | 0%
500 | 368 | 438 | 1 | 26.28 | 26.05 | 60 | 81 | 81 | 3.24 | 12.33% |  | 100% | [5 empty] | 100 | 150
1000 | 368 | 484 | 1 | 29.04 | 28.81 | 60 | 80 | 80 | 6.4 | 22.04% |  | 98.77% | [5 empty] | 200 | 300
3000 | 368 | 751 | 1 | 45.06 | 44.83 | 60 | 78 | 78 | 18.72 | 41.54% |  | 96.3% | [5 empty] | 300 | 450
4000 | 368 | 880 | 1 | 52.8 | 52.57 | 60 | 75 | 75 | 24 | 45.45% |  | 92.59% | [5 empty] | 400 | 600
5000 | 368 | 1047 | 1 | 62.82 | 62.59 | 60 | 75 | 75 | 30 | 47.76% |  | 92.59%
0 | 484 | 500 | 1 | 30 | 29.77 | 60 | 115 | 115 | 0 | 0%
500 | 484 | 581 | 1 | 34.86 | 34.63 | 60 | 110 | 110 | 4.4 | 12.62% |  | 100% | [5 empty] | 100 | 150
1000 | 484 | 660 | 1 | 39.6 | 39.37 | 60 | 105 | 105 | 8.4 | 21.21% |  | 95.45% | [5 empty] | 200 | 300
3000 | 484 | 953 | 1 | 57.18 | 56.95 | 60 | 100 | 100 | 24 | 41.97% |  | 90.91% | [5 empty] | 300 | 450
4000 | 484 | 1105 | 1 | 66.3 | 66.07 | 60 | 100 | 100 | 32 | 48.27% |  | 90.91% | [5 empty] | 400 | 600
5000 | 484 | 1306 | 1 | 78.36 | 78.13 | 60 | 95 | 95 | 38 | 48.49% |  | 86.36%
0 | 600 | 620 | 1 | 37.2 | 36.97 | 60 | 135 | 135 | 0 | 0%
500 | 600 | 710 | 1 | 42.6 | 42.37 | 60 | 130 | 130 | 5.2 | 12.21% |  | 100% | [5 empty] | 100 | 150
1000 | 600 | 809 | 1 | 48.54 | 48.31 | 60 | 130 | 130 | 10.4 | 21.43% |  | 100% | [5 empty] | 200 | 300
3000 | 600 | 1195 | 1 | 71.7 | 71.47 | 60 | 125 | 125 | 30 | 41.84% |  | 96.15% | [5 empty] | 300 | 450
4000 | 600 | 1363 | 1 | 81.78 | 81.55 | 60 | 125 | 125 | 40 | 48.91% |  | 96.15% | [5 empty] | 400 | 600
5000 | 600 | 1453 | 1 | 87.18 | 86.95 | 60 | 110 | 110 | 44 | 50.47% |  | 84.62%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 20 | 136 | 252 | 368 | 484 | 600
[10 empty] | 0 | 5.5 | 34 | 57 | 83 | 115 | 135
[10 empty] | 500 | 5.5 | 32 | 55 | 81 | 110 | 130
[10 empty] | 1000 | 5 | 31 | 55 | 80 | 105 | 130
[10 empty] | 3000 | 4.5 | 29 | 53 | 78 | 100 | 125
[10 empty] | 4000 | 4.5 | 28 | 52 | 75 | 100 | 125
[10 empty] | 5000 | 4 | 27 | 50 | 75 | 95 | 110
[10 empty] | 2040 | 4.8937 | 30.4307 | 53.9182 | 78.9936 | 104.8834 | 126.6255 | L/day
[9 empty] | L/day | 9.4635 | 39.3517 | RPM
CF @ 500 psi | 1230 | L/day
| 600 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 5000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 39.3517
P Corr RPM | 39.3517
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 20 | 136 | 252 | 368 | 484 | 600 | 6000
0 | 0.23 | 2.65 | 11.77 | 16.27 | 22.15 | 29.77 | 36.97 | 369.7 | 4.1714
500 | 0.23 | 3.12 | 12.72 | 18.55 | 26.05 | 34.63 | 42.37 | 423.7 | 4.7215
1000 | 0.23 | 3.84 | 17.22 | 21.43 | 28.81 | 39.37 | 48.31 | 483.1 | 6.0721
3000 | 0.23 | 6.48 | 21.66 | 32.71 | 44.83 | 56.95 | 71.47 | 714.7 | 9.0124
4000 | 0.23 | 10.74 | 25.92 | 39.37 | 52.57 | 66.07 | 81.55 | 815.5 | 13.2724
5000.1 | 0.23 | 14.66 | 31.26 | 46.45 | 62.59 | 78.13 | 86.95 | 869.5 | 17.4293
Enter RPM | 39.3517 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 7.6011 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## F2_500_DH (hidden)
| Date | 2021-05-03 | Tech: Blair Boone
glycol f2-500 - 24V fusion2 motor | [14 empty] | RPMs | pressure
# Heads |  | dual | [12 empty] | 20 | 0
Piston |  | 0.3125 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 136 | 500
Supply V |  | 25.0 V |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 252 | 1000
Stroke |  | 0.136 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 368 | 3000
Head |  | high pressure | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 484 | 4000
head config |  | soft seat cartridge |  |  |  | Maintaining constant RPM | [8 empty] | 600 | 5000
Pressure |  | Power - ELEC |  |  | FLOW |  |  |  | mech work | Effieciency | [7 empty] | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve | [5 empty] | 50 | 75
0 | 20 | 156 | 3 | 3.12 | 2.89 | 180 | 30 | 10 | 0 | 0%
500 | 20 | 204 | 3 | 4.08 | 3.85 | 180 | 29.5 | 9.8333 | 0.39333 | 9.641% |  | 100% | [5 empty] | 100 | 150
1000 | 20 | 240 | 3 | 4.8 | 4.57 | 180 | 28.5 | 9.5 | 0.76 | 15.83% |  | 96.61% | [5 empty] | 200 | 300
3000 | 20 | 612 | 3 | 12.24 | 12.01 | 180 | 27 | 9 | 2.16 | 17.65% |  | 91.53% | [5 empty] | 300 | 450
4000 | 20 | 888 | 3 | 17.76 | 17.53 | 180 | 25.5 | 8.5 | 2.72 | 15.32% |  | 86.44% | [5 empty] | 400 | 600
5000 | 20 | 1188 | 3 | 23.76 | 23.53 | 180 | 24 | 8 | 3.2 | 13.47% |  | 81.36%
0 | 136 | 168 | 1 | 10.08 | 9.85 | 60 | 65 | 65 | 0 | 0%
500 | 136 | 232 | 1 | 13.92 | 13.69 | 60 | 65 | 65 | 2.6 | 18.68% |  | 100% | [5 empty] | 100 | 150
1000 | 136 | 292 | 1 | 17.52 | 17.29 | 60 | 65 | 65 | 5.2 | 29.68% |  | 100% | [5 empty] | 200 | 300
3000 | 136 | 512 | 1 | 30.72 | 30.49 | 60 | 60 | 60 | 14.4 | 46.88% |  | 92.31% | [5 empty] | 300 | 450
4000 | 136 | 660 | 1 | 39.6 | 39.37 | 60 | 55 | 55 | 17.6 | 44.44% |  | 84.62% | [5 empty] | 400 | 600
5000 | 136 | 852 | 1 | 51.12 | 50.89 | 60 | 50 | 50 | 20 | 39.12% |  | 76.92%
0%
0 | 252 | 268 | 1 | 16.08 | 15.85 | 60 | 120 | 120 | 0 | 0%
500 | 252 | 376 | 1 | 22.56 | 22.33 | 60 | 115 | 115 | 4.6 | 20.39% |  | 100% | [5 empty] | 100 | 150
1000 | 252 | 460 | 1 | 27.6 | 27.37 | 60 | 110 | 110 | 8.8 | 31.88% |  | 95.65% | [5 empty] | 200 | 300
3000 | 252 | 804 | 1 | 48.24 | 48.01 | 60 | 100 | 100 | 24 | 49.75% |  | 86.96% | [5 empty] | 300 | 450
4000 | 252 | 996 | 1 | 59.76 | 59.53 | 60 | 95 | 95 | 30.4 | 50.87% |  | 82.61% | [5 empty] | 400 | 600
5000 | 252 | 1260 | 1 | 75.6 | 75.37 | 60 | 90 | 90 | 36 | 47.62% |  | 78.26%
0 | 368 | 410 | 1 | 24.6 | 24.37 | 60 | 170 | 170 | 0 | 0%
500 | 368 | 548 | 1 | 32.88 | 32.65 | 60 | 165 | 165 | 6.6 | 20.07% |  | 100% | [5 empty] | 100 | 150
1000 | 368 | 682 | 1 | 40.92 | 40.69 | 60 | 160 | 160 | 12.8 | 31.28% |  | 96.97% | [5 empty] | 200 | 300
3000 | 368 | 1132 | 1 | 67.92 | 67.69 | 60 | 145 | 145 | 34.8 | 51.24% |  | 87.88% | [5 empty] | 300 | 450
4000 | 368 | 1466 | 1 | 87.96 | 87.73 | 60 | 140 | 140 | 44.8 | 50.93% |  | 84.85% | [5 empty] | 400 | 600
5000 | 368 | 1624 | 1 | 97.44 | 97.21 | 60 | 135 | 135 | 54 | 55.42% |  | 81.82%
0 | 484 | 544 | 1 | 32.64 | 32.41 | 60 | 215 | 215 | 0 | 0%
500 | 484 | 671 | 1 | 40.26 | 40.03 | 60 | 215 | 215 | 8.6 | 21.36% |  | 100% | [5 empty] | 100 | 150
1000 | 484 | 870 | 1 | 52.2 | 51.97 | 60 | 200 | 200 | 16 | 30.65% |  | 93.02% | [5 empty] | 200 | 300
3000 | 484 | 1422 | 1 | 85.32 | 85.09 | 60 | 185 | 185 | 44.4 | 52.04% |  | 86.05% | [5 empty] | 300 | 450
4000 | 484 | 1732 | 1 | 103.92 | 103.69 | 60 | 180 | 180 | 57.6 | 55.43% |  | 83.72% | [5 empty] | 400 | 600
5000 | 484 | 2112 | 1 | 126.72 | 126.49 | 60 | 175 | 175 | 70 | 55.24% |  | 81.4%
0 | 600 | 630 | 1 | 37.8 | 37.57 | 60 | 280 | 280 | 0 | 0%
500 | 600 | 834 | 1 | 50.04 | 49.81 | 60 | 270 | 270 | 10.8 | 21.58% |  | 100% | [5 empty] | 100 | 150
1000 | 600 | 998 | 1 | 59.88 | 59.65 | 60 | 255 | 255 | 20.4 | 34.07% |  | 94.44% | [5 empty] | 200 | 300
3000 | 600 | 1796 | 1 | 107.76 | 107.53 | 60 | 230 | 230 | 55.2 | 51.22% |  | 85.19% | [5 empty] | 300 | 450
4000 | 600 | 2080 | 1 | 124.8 | 124.57 | 60 | 225 | 225 | 72 | 57.69% |  | 83.33% | [5 empty] | 400 | 600
5000 | 600 | 2408 | 1 | 144.48 | 144.25 | 60 | 215 | 215 | 86 | 59.52% |  | 79.63%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 20 | 136 | 252 | 368 | 484 | 600
[10 empty] | 0 | 10 | 65 | 120 | 170 | 215 | 280
[10 empty] | 500 | 9.8333 | 65 | 115 | 165 | 215 | 270
[10 empty] | 1000 | 9.5 | 65 | 110 | 160 | 200 | 255
[10 empty] | 3000 | 9 | 60 | 100 | 145 | 185 | 230
[10 empty] | 4000 | 8.5 | 55 | 95 | 140 | 180 | 225
[10 empty] | 5000 | 8 | 50 | 90 | 135 | 175 | 215
[10 empty] | 2040 | 9.2189 | 60.6287 | 106.2072 | 153.9713 | 196.7605 | 248.4866 | L/day
[9 empty] | L/day | 9.4635 | 15.9627 | RPM
CF @ 500 psi | 1230 | L/day
| 600 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 5000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 15.9627
P Corr RPM | 15.9627
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 20 | 136 | 252 | 368 | 484 | 600 | 6000
0 | 0.23 | 2.89 | 9.85 | 15.85 | 24.37 | 32.41 | 37.57 | 375.7 | 2.3503
500 | 0.23 | 4.08 | 13.92 | 22.33 | 32.65 | 40.03 | 49.81 | 498.1 | 3.2989
1000 | 0.23 | 4.8 | 17.52 | 27.37 | 40.69 | 51.97 | 59.65 | 596.5 | 3.8728
3000 | 0.23 | 12.24 | 30.72 | 48.01 | 67.69 | 85.09 | 107.53 | 1075.3 | 9.8034
4000 | 0.23 | 17.76 | 39.6 | 59.53 | 87.73 | 103.69 | 124.57 | 1245.7 | 14.2035
5000.1 | 0.23 | 23.76 | 51.12 | 75.37 | 97.21 | 126.49 | 144.25 | 1442.5 | 18.9862
Enter RPM | 15.9627 | RPM
Enter Pressure | 2040 | psi
Calc Watts | 6.9567 | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## DH -COMET_100 (hidden)
| Date | 2021-03-11 | Tech: Blair Boone
glycol COMET_100 pump - 24V comet motor | [14 empty] | RPMs | pressure
# Heads |  | Dual | [12 empty] | 100 | 0
Piston |  | 0.625 |  |  |  | Quiescent | mA |  | Watts | [5 empty] | 200 | 100 |  | min rpm
Supply V |  | 25.0 V |  |  |  | Display on | 73.5 |  | 1.8375 | Do not change |  |  |  |  | 400 | 250 |  | 300
Stroke |  | 0.136 |  |  |  | Display off | 64.3 |  | 1.6075 | Do not change |  |  |  |  | 600 | 500
Head |  | HIGH VOLUME | [5 empty] | Display | 0.23 | Watts | Fixed for F2 controller |  |  |  | 800 | 750
head config |  | soft seat poppet suction, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 1000 | 1000
Pressure |  | Power - ELEC |  |  | FLOW |  |  | measured | mech work | Effieciency |  |  |  |  | average rate |  |  |  | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve |  | duty cycle | L/d |  |  |  | 50 | 75
0 | 100 | 411 | 4 | 6.165 | 5.935 | 37.09 | 300 | 485.306 | 0 | 0% |  |  |  | 33.33% | 161.7687
100 | 100 | 620 | 4 | 9.3 | 9.07 | 42.47 | 300 | 423.8286 | 3.3906 | 36.46% |  | 100% |  | 33.33% | 141.2762 |  |  |  | 100 | 150
250 | 100 | 776 | 4 | 11.64 | 11.41 | 45.26 | 300 | 397.7022 | 7.954 | 68.33% |  | 93.84% |  | 33.33% | 132.5674 |  |  |  | 200 | 300
500 | 100 | 904 | 4 | 13.56 | 13.33 | 49.49 | 300 | 363.7098 | 14.5484 | 107.3% |  | 85.82% |  | 33.33% | 121.2366 |  |  |  | 300 | 450
750 | 100 | 1166 | 4 | 17.49 | 17.26 | 53.73 | 300 | 335.0084 | 20.1005 | 114.9% |  | 79.04% |  | 33.33% | 111.6695 |  |  |  | 400 | 600
1000 | 100 | 1560 | 4 | 23.4 | 23.17 | 61 | 300 | 295.082 | 23.6066 | 100.9% |  | 69.62% |  | 33.33% | 98.3607
0 | 200 | 820 | 4 | 12.3 | 12.07 | 59.62 | 500 | 503.1869 | 0 | 0% |  |  |  | 66.67% | 335.4579
100 | 200 | 1231 | 4 | 18.465 | 18.235 | 69 | 500 | 434.7826 | 3.4783 | 18.84% |  | 100% |  | 66.67% | 289.8551 |  |  |  | 100 | 150
250 | 200 | 1546 | 4 | 23.19 | 22.96 | 74 | 500 | 405.4054 | 8.1081 | 34.96% |  | 93.24% |  | 66.67% | 270.2703 |  |  |  | 200 | 300
500 | 200 | 1909 | 4 | 28.635 | 28.405 | 81.71 | 500 | 367.1521 | 14.6861 | 51.29% |  | 84.44% |  | 66.67% | 244.7681 |  |  |  | 300 | 450
750 | 200 | 2400 | 4 | 36 | 35.77 | 90 | 500 | 333.3333 | 20 | 55.56% |  | 76.67% |  | 66.67% | 222.2222 |  |  |  | 400 | 600
1000 | 200 | 3074 | 4 | 46.11 | 45.88 | 102.72 | 500 | 292.0561 | 23.3645 | 50.67% |  | 67.17% |  | 66.67% | 194.704
0 | 400 | 397 | 1 | 23.82 | 23.59 | 66.38 | 800 | 723.1094 | 0 | 0%
100 | 400 | 570 | 1 | 34.2 | 33.97 | 68.88 | 800 | 696.8641 | 5.5749 | 16.3% |  | 100% | [6 empty] | 100 | 150
250 | 400 | 744 | 1 | 44.64 | 44.41 | 75.62 | 800 | 634.7527 | 12.6951 | 28.44% |  | 91.09% | [6 empty] | 200 | 300
500 | 400 | 997 | 1 | 59.82 | 59.59 | 88.59 | 800 | 541.8219 | 21.6729 | 36.23% |  | 77.75% | [6 empty] | 300 | 450
750 | 400 | 1125 | 1 | 67.5 | 67.27 | 99.93 | 800 | 480.3362 | 28.8202 | 42.7% |  | 68.93% | [6 empty] | 400 | 600
1000 | 400 | 1477 | 1 | 88.62 | 88.39 | 109.72 | 800 | 437.4772 | 34.9982 | 39.49% |  | 62.78%
0 | 600 | 608 | 1 | 36.48 | 36.25 | 61.75 | 1200 | 1165.9919 | 0 | 0%
100 | 600 | 877 | 1 | 52.62 | 52.39 | 69.88 | 1200 | 1030.3377 | 8.2427 | 15.66% |  | 100% | [6 empty] | 100 | 150
250 | 600 | 1076 | 1 | 64.56 | 64.33 | 75.48 | 1200 | 953.8951 | 19.0779 | 29.55% |  | 92.58% | [6 empty] | 200 | 300
500 | 600 | 1242 | 1 | 74.52 | 74.29 | 80.62 | 1200 | 893.0786 | 35.7231 | 47.94% |  | 86.68% | [6 empty] | 300 | 450
750 | 600 | 1558 | 1 | 93.48 | 93.25 | 88.98 | 1200 | 809.1706 | 48.5502 | 51.94% |  | 78.53% | [6 empty] | 400 | 600
1000 | 600 | 2003 | 1 | 120.18 | 119.95 | 100.06 | 1200 | 719.5683 | 57.5655 | 47.9% |  | 69.84%
0 | 800 | 892 | 1 | 53.52 | 53.29 | 41.43 | 1100 | 1593.0485 | 0 | 0%
100 | 800 | 1190 | 1 | 71.4 | 71.17 | 45.05 | 1100 | 1465.0388 | 11.7203 | 16.42% |  | 100% | [6 empty] | 100 | 150
250 | 800 | 1492 | 1 | 89.52 | 89.29 | 48.34 | 1100 | 1365.3289 | 27.3066 | 30.5% |  | 93.19% | [6 empty] | 200 | 300
500 | 800 | 1731 | 1 | 103.86 | 103.63 | 51.91 | 1100 | 1271.4313 | 50.8573 | 48.97% |  | 86.78% | [6 empty] | 300 | 450
750 | 800 | 2062 | 1 | 123.72 | 123.49 | 57.09 | 1100 | 1156.0694 | 69.3642 | 56.07% |  | 78.91% | [6 empty] | 400 | 600
1000 | 800 | 2512 | 1.05 | 143.5429 | 143.3129 | 64.42 | 1100 | 1024.5265 | 81.9621 | 57.1% |  | 69.93%
0 | 1000 | 1176 | 1 | 70.56 | 70.33 | 47 | 1600 | 2042.5532 | 0 | 0%
100 | 1000 | 1572 | 1 | 94.32 | 94.09 | 51.2 | 1600 | 1875 | 15 | 15.9% |  | 100% | [6 empty] | 100 | 150
250 | 1000 | 1944 | 1 | 116.64 | 116.41 | 54.56 | 1600 | 1759.5308 | 35.1906 | 30.17% |  | 93.84% | [6 empty] | 200 | 300
500 | 1000 | 2302 | 1 | 138.12 | 137.89 | 57.55 | 1600 | 1668.1147 | 66.7246 | 48.31% |  | 88.97% | [6 empty] | 300 | 450
750 | 1000 | 2908 | 1.05 | 166.1714 | 165.9414 | 65.62 | 1600 | 1462.9686 | 87.7781 | 52.82% |  | 78.02% | [6 empty] | 400 | 600
1000 | 1000 | 3184 | 1 | 191.04 | 190.81 | 72.95 | 1600 | 1315.9698 | 105.2776 | 55.11% |  | 70.19%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 100 | 200 | 400 | 600 | 800 | 1000
[10 empty] | 0 | 161.7687 | 335.4579 | 723.1094 | 1165.9919 | 1593.0485 | 2042.5532
[10 empty] | 100 | 141.2762 | 289.8551 | 696.8641 | 1030.3377 | 1465.0388 | 1875
[10 empty] | 250 | 132.5674 | 270.2703 | 634.7527 | 953.8951 | 1365.3289 | 1759.5308
[10 empty] | 500 | 121.2366 | 244.7681 | 541.8219 | 893.0786 | 1271.4313 | 1668.1147
[10 empty] | 750 | 111.6695 | 222.2222 | 480.3362 | 809.1706 | 1156.0694 | 1462.9686
[10 empty] | 1000 | 98.3607 | 194.704 | 437.4772 | 719.5683 | 1024.5265 | 1315.9698
[10 empty] | 2040 | 38.1639 | 59.3045 | 107.1696 | 292.9453 | 470.2671 | 601.5537 | L/day
[9 empty] | L/day | 9.4635 | 148.5684 | RPM
CF @ 500 psi | 1670 | L/day | [10 empty] | watts | flow | watts | flow
| 1000 | RPM | [10 empty] | 5.935 | 161.7687 | 12.07 | 335.4579
Enter Flow | 9.4635 | L/day | [10 empty] | 9.3 | 141.2762 | 18.465 | 289.8551
Enter pressure | 2040 | 1000 | max | [9 empty] | 11.64 | 132.5674 | 23.19 | 270.2703
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom | [8 empty] | 13.56 | 121.2366 | 28.635 | 244.7681
Calc RPM | 148.5684 | [11 empty] | 17.49 | 111.6695 | 36 | 222.2222
P Corr RPM | 148.5684 | [11 empty] | 23.4 | 98.3607 | 46.11 | 194.704
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 100 | 200 | 400 | 600 | 800 | 1000 | 10000
0 | 0.23 | 5.935 | 12.07 | 23.59 | 36.25 | 53.29 | 70.33 | 703.3 | 8.9147
100 | 0.23 | 9.3 | 18.465 | 33.97 | 52.39 | 71.17 | 94.09 | 940.9 | 13.7513
250 | 0.23 | 11.64 | 23.19 | 44.41 | 64.33 | 89.29 | 116.41 | 1164.1 | 17.2496
500 | 0.23 | 13.56 | 28.635 | 59.59 | 74.29 | 103.63 | 137.89 | 1378.9 | 20.8817
750 | 0.23 | 17.49 | 36 | 67.27 | 93.25 | 123.49 | 165.9414 | 1659.4143 | 26.48
1000.1 | 0.23 | 23.4 | 46.11 | 88.39 | 119.95 | 143.3129 | 190.81 | 1908.1 | 34.4299
Enter RPM | 148.5684 | RPM
Enter Pressure | 2040 | psi
Calc Watts | #DIV/0! | Watts
[10 empty] | 98.3607 | 194.704 | 437.4772 | 719.5683 | 1024.5265 | 1315.9698
[10 empty] | 100 | 200 | 400 | 600 | 800 | 1000
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'

## DH -F2_100 (hidden)
| Date | 2021-03-24 | Tech: Blair Boone
glycol COMET_100 pump - 24V fusion2 motor | [14 empty] | RPMs | pressure
# Heads |  | Dual |  |  |  |  | mWhr | min | Watts | [5 empty] | 20 | 0
Piston |  | 0.625 |  |  |  | Quiescent | [8 empty] | 136 | 100
Supply V |  | 25.0 V |  |  |  | Display on | 105 | 3 | 2.1 | [5 empty] | 252 | 250
Stroke |  | 0.136 |  |  |  | Display off | 87 | 3 | 1.74 | [5 empty] | 368 | 500
Head |  | HIGH VOLUME | [5 empty] | Display | 0.36 | Watts |  |  |  |  | 484 | 750
head config |  | soft seat poppet suction, soft seat discharge |  |  |  | Maintaining constant RPM | [8 empty] | 600 | 1000
Pressure |  | Power - ELEC |  |  | FLOW |  |  |  | mech work | Effieciency | [7 empty] | 10 | 15
PSI | RPM | mWhr | Sample Time(min) | Watts | Disp off Watts | time sec | draw L | Rate L/day | Watts | n |  | Pump curve | [5 empty] | 50 | 75
0 | 20 | 61 | 1 | 3.66 | 3.3 | 252 | 200 | 47.619 | 0 | 0%
100 | 20 | 108 | 1 | 6.48 | 6.12 | 254 | 200 | 47.2441 | 0.37795 | 5.833% |  | 100% | [5 empty] | 100 | 150
250 | 20 | 148 | 1 | 8.88 | 8.52 | 255 | 200 | 47.0588 | 0.94118 | 10.6% |  | 99.61% | [5 empty] | 200 | 300
500 | 20 | 175 | 1 | 10.5 | 10.14 | 257 | 200 | 46.6926 | 1.8677 | 17.79% |  | 98.83% | [5 empty] | 300 | 450
750 | 20 | 234 | 1 | 14.04 | 13.68 | 257 | 200 | 46.6926 | 2.8016 | 19.95% |  | 98.83% | [5 empty] | 400 | 600
1000 | 20 | 326 | 1 | 19.56 | 19.2 | 257 | 200 | 46.6926 | 3.7354 | 19.1% |  | 98.83%
0 | 136 | 201 | 1 | 12.06 | 11.7 | 110 | 500 | 272.7273 | 0 | 0%
100 | 136 | 290 | 1 | 17.4 | 17.04 | 111 | 500 | 270.2703 | 2.1622 | 12.43% |  | 100% | [5 empty] | 100 | 150
250 | 136 | 381 | 1 | 22.86 | 22.5 | 111 | 500 | 270.2703 | 5.4054 | 23.65% |  | 100% | [5 empty] | 200 | 300
500 | 136 | 479 | 1 | 28.74 | 28.38 | 112 | 500 | 267.8571 | 10.7143 | 37.28% |  | 99.11% | [5 empty] | 300 | 450
750 | 136 | 593 | 1 | 35.58 | 35.22 | 113 | 500 | 265.4867 | 15.9292 | 44.77% |  | 98.23% | [5 empty] | 400 | 600
1000 | 136 | 767 | 1 | 46.02 | 45.66 | 114 | 500 | 263.1579 | 21.0526 | 45.75% |  | 97.37%
0%
0 | 252 | 327 | 1 | 19.62 | 19.26 | 71 | 600 | 507.0423 | 0 | 0%
100 | 252 | 547 | 1 | 32.82 | 32.46 | 72 | 600 | 500 | 4 | 12.19% |  | 100% | [5 empty] | 100 | 150
250 | 252 | 653 | 1 | 39.18 | 38.82 | 60 | 500 | 500 | 10 | 25.52% |  | 100% | [5 empty] | 200 | 300
500 | 252 | 784 | 1 | 47.04 | 46.68 | 60 | 500 | 500 | 20 | 42.52% |  | 100% | [5 empty] | 300 | 450
750 | 252 | 1016 | 1 | 60.96 | 60.6 | 73 | 600 | 493.1507 | 29.589 | 48.54% |  | 98.63% | [5 empty] | 400 | 600
1000 | 252 | 1241 | 1 | 74.46 | 74.1 | 61 | 500 | 491.8033 | 39.3443 | 52.84% |  | 98.36%
0 | 368 | 440 | 1 | 26.4 | 26.04 | 64 | 800 | 750 | 0 | 0%
100 | 368 | 694 | 1 | 41.64 | 41.28 | 64 | 800 | 750 | 6 | 14.41% |  | 100% | [5 empty] | 100 | 150
250 | 368 | 873 | 1 | 52.38 | 52.02 | 65 | 800 | 738.4615 | 14.7692 | 28.2% |  | 98.46% | [5 empty] | 200 | 300
500 | 368 | 1082 | 1 | 64.92 | 64.56 | 66 | 800 | 727.2727 | 29.0909 | 44.81% |  | 96.97% | [5 empty] | 300 | 450
750 | 368 | 1346 | 1 | 80.76 | 80.4 | 67 | 800 | 716.4179 | 42.9851 | 53.23% |  | 95.52% | [5 empty] | 400 | 600
1000 | 368 | 1745 | 1 | 104.7 | 104.34 | 68 | 800 | 705.8824 | 56.4706 | 53.94% |  | 94.12%
0 | 484 | 950 | 1.55 | 36.7742 | 36.4142 | 62 | 1000 | 967.7419 | 0 | 0%
100 | 484 | 1352 | 1.3833 | 58.641 | 58.281 | 62 | 1000 | 967.7419 | 7.7419 | 13.2% |  | 100% | [5 empty] | 100 | 150
250 | 484 | 1173 | 1 | 70.38 | 70.02 | 69 | 1000 | 869.5652 | 17.3913 | 24.71% |  | 89.86% | [5 empty] | 200 | 300
500 | 484 | 1405 | 1 | 84.3 | 83.94 | 69 | 1000 | 869.5652 | 34.7826 | 41.26% |  | 89.86% | [5 empty] | 300 | 450
750 | 484 | 1692 | 1 | 101.52 | 101.16 | 70 | 1000 | 857.1429 | 51.4286 | 50.66% |  | 88.57% | [5 empty] | 400 | 600
1000 | 484 | 2174 | 1 | 130.44 | 130.08 | 65 | 1000 | 923.0769 | 73.8462 | 56.61% |  | 95.38%
0 | 600 | 1156 | 1.4667 | 47.2909 | 46.9309 | 64 | 1300 | 1218.75 | 0 | 0%
100 | 600 | 1874 | 1.5 | 74.96 | 74.6 | 64 | 1300 | 1218.75 | 9.75 | 13.01% |  | 100% | [5 empty] | 100 | 150
250 | 600 | 2596 | 1.7333 | 89.8615 | 89.5015 | 65 | 1300 | 1200 | 24 | 26.71% |  | 98.46% | [5 empty] | 200 | 300
500 | 600 | 4190 | 2.4 | 104.75 | 104.39 | 64 | 1300 | 1218.75 | 48.75 | 46.54% |  | 100% | [5 empty] | 300 | 450
750 | 600 | 2195 | 1 | 131.7 | 131.34 | 61 | 1200 | 1180.3279 | 70.8197 | 53.77% |  | 96.85% | [5 empty] | 400 | 600
1000 | 600 | 2788 | 1 | 167.28 | 166.92 | 62 | 1200 | 1161.2903 | 92.9032 | 55.54% |  | 95.29%
[11 empty] | RPM |  | Flow Table ( L/day)
[10 empty] | Pressure | 20 | 136 | 252 | 368 | 484 | 600
[10 empty] | 0 | 47.619 | 272.7273 | 507.0423 | 750 | 967.7419 | 1218.75
[10 empty] | 100 | 47.2441 | 270.2703 | 500 | 750 | 967.7419 | 1218.75
[10 empty] | 250 | 47.0588 | 270.2703 | 500 | 738.4615 | 869.5652 | 1200
[10 empty] | 500 | 46.6926 | 267.8571 | 500 | 727.2727 | 869.5652 | 1218.75
[10 empty] | 750 | 46.6926 | 265.4867 | 493.1507 | 716.4179 | 857.1429 | 1180.3279
[10 empty] | 1000 | 46.6926 | 263.1579 | 491.8033 | 705.8824 | 923.0769 | 1161.2903
[10 empty] | 2040 | 45.6177 | 253.9499 | 477.7644 | 657.113 | 805.5794 | 1112.1644 | L/day
[9 empty] | L/day | 9.4635 | 1.3227 | RPM
CF @ 500 psi | 1230 | L/day
| 600 | RPM
Enter Flow | 9.4635 | L/day
Enter pressure | 2040 | 1000 | max
Pcor | 0 | avg slope of Pump Curve |  | 0.11 nom
Calc RPM | 1.3227
P Corr RPM | 1.3227
Interpolation Table
Pressure |  |  |  | Watts Table |  |  | Interm
RPM | 0.1 | 20 | 136 | 252 | 368 | 484 | 600 | 6000
0 | 0.36 | 3.3 | 11.7 | 19.26 | 26.04 | 36.4142 | 46.9309 | 469.3091 | 0.54065
100 | 0.36 | 6.48 | 17.4 | 32.46 | 41.28 | 58.281 | 74.6 | 746 | 0.73604
250 | 0.36 | 8.88 | 22.86 | 38.82 | 52.02 | 70.02 | 89.5015 | 895.0154 | 0.8835
500 | 0.36 | 10.5 | 28.74 | 46.68 | 64.56 | 83.94 | 104.39 | 1043.9 | 0.98304
750 | 0.36 | 14.04 | 35.58 | 60.6 | 80.4 | 101.16 | 131.34 | 1313.4 | 1.2006
1000.1 | 0.36 | 19.56 | 46.02 | 74.1 | 104.34 | 130.08 | 166.92 | 1669.2 | 1.5397
Enter RPM | 1.3227 | RPM
Enter Pressure | 2040 | psi
Calc Watts | #DIV/0! | Watts
Note on B83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Kirby Jabusch you've got a 'pressure corrected RPM value here calculation baked in to this spreadsheet, however based on how we pulled this data, I believe that we can leave this correction value at '0'